83022 LED CG-S
Pos.    )		ea.

Safety luminaire with high protection class (IP65) in LED technology for ceiling or wall mounting. In line with EN 60598-1, EN 60598-2-22 and EN 1838 for operation on emergency lighting systems in line with EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100. Developed, manufactured and tested in line with ISO 9001.

Robust square construction from aluminium diecast with powder coating.
Two waterproof cable infeeds (IP67).
Double terminal for through-wiring.
Impact-resistant diffuser made of UV-stabilized polycarbonate (IK08).

Symmetric optics for uniform open area illumination with at least 1 lx acc. EN 1838 for mounting heights of up to 10 m.
Maximum spacing between luminaries:
>11 m as form 3 m mounting height.
>15.5 m as from 7 m mounting height.
(Basis of calculation: room illumination with at least 1 lx, maintenance factor = 0.8)

Light source: 42 efficient, white high-power LEDs with a service life of up to 50,000 h on account of optimised LED operating conditions.

Specialised LED-Converter with integrated single luminaire monitoring module and 20-digit address switch (CEWA GUARD Technology). Freely programmable mixed operation (maintained, non-maintained and switched maintained mode) without additional data line or wiring required for the luminaires connected to the relevant emergency lighting system with STAR Technology.
Including Single LED monitoring Intelligence (SLI Technology).

Luminous flux:						620 lm
Luminous flux at the end
of the rated service time (EBLF):				100%
Housing material:					Housing: Aluminium diecast
Cover: Polycarbonate
Housing colour:						White RAL 9010
Connection terminal:					2 x 3 x 2.5 mm²
Supply voltage:						220 - 240 V AC, 50/60 Hz // 176 - 275 V DC
Power Consumption incl. LED supply
[bookmark: _GoBack](apparent power / effective power):			16.87 VA / 9.6 W
Current consumption - battery operation (220V):		48 mA
Protection class:					1
Impact Resistance:					IK08 (Cover)
Protection type:						IP65
Permissible ambient temperature:			-20°C to +40°C
Light source:						42 x 180 mW Low Power LEDs, 4000K
Dimensions (mm):					L = 270, H = 270; W = 60

Accessories:
… pcs. Pictogram-set for 83022 acc. to ISO 7010, arrow left, right, down

Luminaire with ENEC certification mark, confirmed by independent audit body.

Type: CEAG 83022 LED CG-S
Manufacturer: Eaton
