## Setpoint (holding)
Modbus setpoints P631 | holding register | Microbooster Firmware 1.5 18-05-2021
Modbus Code | Parameter | Read/Write (D02.4 Modbus modify = 0) | Read/Write (D02.4 Modbus modify = 1) | Data Type | Raw minimum value | Raw maximum value | Min value | Max Value | Format | Unit | Comment | Page in manual
4x0000 | P Mode (0=AUTO 1=ECO 2=BOOST 3=BACK-UP 4=HOLIDAY) | R | R/W | uint16 | 0 | 4 | 0 | 4 | *1 |  | Information is given in manual | 29
4x0001 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0002 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0003 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0004 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0005 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0006 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0007 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0008 | A1 T AUTO | R | R/W | int16 | 50 | 650 | 5 | 65 | *10 | °C | Information is given in manual | 30
4x0009 | A2 T ECO | R | R/W | int16 | 50 | 550 | 5 | 55 | *10 | °C | Information is given in manual | 30
4x0010 | A3 T BOOST | R | R/W | int16 | 50 | 650 | 5 | 65 | *10 | °C | Information is given in manual | 30
4x0011 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0012 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0013 |  | R | R/W | uint16 | 0 | 2 | 0 | 2 | *1
4x0014 | B01 Source flow control (0=AUTO 1=FIXED 2=DELTA T 3=RETURN T) | R | R/W | uint16 | 0 | 3 | 0 | 3 | *1 |  | Information is given in manual | 31
4x0015 | B02 Low tariff (0=OFF, 1=Standart,2=EL optimal 1, 3=EL optimal 2) | R | R/W | uint16 | 0 | 3 | 0 | 3 | *1 |  | Information is given in manual | 32
4x0016 | B03 Hot on time | R | R/W | uint16 | 0 | 30 | 0 | 30 | *1 | Days | Information is given in manual | 32
4x0017 | B05 PV (0=OFF, 1=ECO, 2=STORAGE) | R | R/W | uint16 | 0 | 2 | 0 | 2 | *1 |  | Information is given in manual | 32
4x0018 |  | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF
4x0019 |  | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF
4x0020 |  | R | R/W | uint16 | 50 | 500 | 5 | 50 | *10 | °C
4x0021 |  | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF
4x0022 |  | R | R/W | uint16 | 100 | 300 | 10 | 30 | *10 | °C
4x0023 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0024 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0025 | C0 Reset (1=RESET) | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Information is given in manual | 33
4x0026 | C1.1 Model | R | R | uint16 | 0 | 65535 | 0 | 65535 | *1 | Seconds | Information is given in manual | 33
4x0027 | C1.2 Software | R | R | uint16 | 0 | 65530 | 0 | 6553 | *10 | Seconds | Information is given in manual | 33
4x0028 |  | R | R/W | uint16 | 0 | 65535 | 0 | 65535 | *1
4x0029 | C2.1 Hour | R | R/W | uint16 | 0 | 23 | 0 | 23 | *1 | Hours | Information is given in manual | 33
4x0030 | C2.2 Minutes | R | R/W | uint16 | 0 | 59 | 0 | 59 | *1 | Minuten | Information is given in manual | 33
4x0031 | C3.1 Date | R | R/W | uint16 | 0 | 31 | 0 | 31 | *1 |  | Information is given in manual | 33
4x0032 | C3.2 Month | R | R/W | uint16 | 1 | 12 | 1 | 12 | *1 |  | Information is given in manual | 33
4x0033 | C3.3 Year | R | R/W | uint16 | 0 | 99 | 0 | 99 | *1 |  | Information is given in manual | 33
4x0034 | C4 Day | R | R/W | uint16 | 1 | 7 | 1 | 7 | *1 | ON/OFF | Information is given in manual | 33
4x0035 | C5 Language (0=UK, 1=DE, 2=FR, 3=DK, 4=NL, 5=PL, 6=ITA) | R | R/W | uint16 | 0 | 6 | 0 | 6 | *1 |  | Information is given in manual | 33
4x0036 | C6 Contrast | R | R/W | uint16 | 0 | 8 | 0 | 8 | *1 |  | Information is given in manual | 33
4x0037 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0038 | D0 Reset All (1=RESET) | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Information is given in manual | 34
4x0039 | D02.1 Modbus address | R | R/W | uint16 | 1 | 247 | 1 | 247 | *1 |  | Information is given in manual | 34
4x0040 | D02.2 Modbus baud rate (0=9600 , 1 = 19200) | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 |  | Information is given in manual | 34
4x0041 | D02.3 Modbus parity (0 = NONE, 1 = EVEN, 2 = ODD) | R | R/W | uint16 | 0 | 2 | 0 | 2 | *1 |  | Information is given in manual | 34
4x0042 | D02.4 Modbus modify (0=Write disabled) | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Information is given in manual | 34
4x0043 | D03 Source flow max | R | R/W | uint16 | 0 | 100 | 0 | 100 | *1 | % | Information is given in manual | 34
4x0044 | D04 Source flow min | R | R/W | uint16 | 0 | 100 | 0 | 100 | *1 | % | Information is given in manual | 34
4x0045 | D05 DELTA T Source | R | R/W | int16 | -200 | 200 | -20 | 20 | *10 | °C | Information is given in manual | 34
4x0046 | D06 Return T | R | R/W | int16 | -200 | 500 | -20 | 50 | *10 | °C | Information is given in manual | 34
4x0047 | D07 Source T min | R | R/W | int16 | -150 | 300 | -15 | 30 | *10 | °C | Information is given in manual | 35
4x0048 | D08 Source T max | R | R/W | int16 | 200 | 890 | 20 | 89 | *10 | °C | Information is given in manual | 35
4x0049 | D09 Water T max | R | R/W | int16 | 500 | 700 | 50 | 70 | *10 | °C | Information is given in manual | 35
4x0050 | D10 Evaporator T max | R | R/W | int16 | 200 | 600 | 20 | 60 | *10 | °C | Information is given in manual | 35
4x0051 | D11 Evaporator T min | R | R/W | int16 | -200 | 200 | -20 | 20 | *10 | °C | Information is given in manual | 35
4x0052 | D12 Backup T | R | R/W | int16 | 50 | 650 | 5 | 65 | *10 | °C | Information is given in manual | 35
4x0053 | D13 Legionella (1=ON) | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Information is given in manual | 35
4x0054 | D14 Legionella T | R | R/W | int16 | 550 | 650 | 55 | 65 | *10 | °C | Information is given in manual | 35
4x0055 | D15 Legionella day (1 = Monday 2=Tuesday .. etc.) | R | R/W | uint16 | 1 | 7 | 1 | 7 | *1 | Days | Information is given in manual | 35
4x0056 | D16 Forced operation (1=ON) | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Information is given in manual | 36
4x0057 | D17.1 Low tariff week-day start hour#1 (-1 = OFF) | R | R/W | int16 | -1 | 23 | -1 | 23 | *1 |  | Information is given in manual | 36
4x0058 | D17.2 Low tariff week-day end hour#1 | R | R/W | int16 | 0 | 23 | 0 | 23 | *1 |  | Information is given in manual | 36
4x0059 | D17.3 Low tariff week-day start hour#2 (-1 = OFF) | R | R/W | int16 | -1 | 23 | -1 | 23 | *1 |  | Information is given in manual | 36
4x0060 | D17.4 Low tariff week-day end hour#2 | R | R/W | int16 | 0 | 23 | 0 | 23 | *1 |  | Information is given in manual | 36
4x0061 | D17.5 Low tariff week-day start hour#3 (-1 = OFF) | R | R/W | int16 | -1 | 23 | -1 | 23 | *1 |  | Information is given in manual | 36
4x0062 | D17.6 Low tariff week-day end hour#3 | R | R/W | int16 | 0 | 23 | 0 | 23 | *1 |  | Information is given in manual | 36
4x0063 | D18.1 Low tariff week-end start hour#1 (-1 = OFF) | R | R/W | int16 | -1 | 23 | -1 | 23 | *1 |  | Information is given in manual | 36
4x0064 | D18.2 Low tariff week-end end hour#1 | R | R/W | int16 | 0 | 23 | 0 | 23 | *1 |  | Information is given in manual | 36
4x0065 | D18.3 Low tariff week-end start hour#2 (-1 = OFF) | R | R/W | int16 | -1 | 23 | -1 | 23 | *1 |  | Information is given in manual | 36
4x0066 | D18.4 Low tariff week-end end hour#2 | R | R/W | int16 | 0 | 23 | 0 | 23 | *1 |  | Information is given in manual | 36
4x0067 | D18.5 Low tariff week-end start hour#3 (-1 = OFF) | R | R/W | int16 | -1 | 23 | -1 | 23 | *1 |  | Information is given in manual | 36
4x0068 | D18.6 Low tariff week-end end hour#3 | R | R/W | int16 | 0 | 23 | 0 | 23 | *1 |  | Information is given in manual | 36
4x0069 | D19 Daylight Saving Time(1=ON) | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Information is given in manual | 36
4x0070 | D20 PV min voltage HP | R | R/W | uint16 | 0 | 100 | 0 | 10 | *10 | Volt | Information is given in manual | 36
4x0071 | D21 PV min voltage EL | R | R/W | uint16 | 0 | 100 | 0 | 10 | *10 | Volt | Information is given in manual | 36
4x0072 | D22 PV min time | R | R/W | uint16 | 0 | 99 | 0 | 99 | *1 | Minuten | Information is given in manual | 36
4x0073 | D23 SG ready (1=ON) | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Information is given in manual | 37
4x0074 | D24 External control (0=OFF, 1=Start/Stop) | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 |  | Information is given in manual | 37
4x0075 | D25 Service timer (0=OFF 1=ON) | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Information is given in manual | 37
4x0076 | D26 Service interval | R | R/W | uint16 | 0 | 36 | 0 | 36 | *1 | Months | Information is given in manual | 37
4x0077 | D27 Service reset | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Information is given in manual | 37
4x0078 | D28 T HP Max | R | R/W | int16 | 550 | 700 | 55 | 70 | *10 | °C | Information is given in manual | 37
4x0079 |  | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF
4x0080 | D29 Demo Mode | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Information is given in manual | 37
4x0081 | D30 Preheat hysteresis | R | R/W | int16 | -200 | 200 | -20 | 20 | *10 | °C | Information is given in manual | 37
4x0082 | D31 Preheat (Coil) | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Information is given in manual | 37
4x0083 | D32 Interim (Coil + HP) | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Information is given in manual | 38
4x0084 | D33 Pump / Valve (0 = Valve, 1=Pump) | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 |  | Information is given in manual | 38
4x0085 | D34 Water hysteresis | R | R/W | int16 | 10 | 200 | 1 | 20 | *10 | °C | Information is given in manual | 38
4x0086 | D35 Brine (0=OFF 1=ON) | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Information is given in manual | 38
4x0087 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1 |  | Information is given in manual | 38
4x0088 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0089 | M01 Time flow increase | R | R/W | uint16 | 0 | 120 | 0 | 120 | *1 | Seconds | Only for development
4x0090 | M02 Time flow decrease | R | R/W | uint16 | 0 | 120 | 0 | 120 | *1 | Seconds | Only for development
4x0091 | M04 Auxiliary Pump | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Only for development
4x0092 | M03 DELTA T preheat | R | R/W | int16 | 0 | 500 | 0 | 50 | *10 | °C | Only for development
4x0093 | M05 Password | R | R/W | uint16 | 0 | 9999 | 0 | 9999 | *1 |  | Only for development
4x0094 | M06 Reset Event Log | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Only for development
4x0095 | M07 Save Restore Setpoints (1=RestoreFromBackup, 2=SaveToBackup, 3=RestoreFirstTimeReset) | R | R/W | uint16 | 0 | 3 | 0 | 3 | *1 |  | Only for development
4x0096 | M08 PVT Booster | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Only for development
4x0097 | M09 External Pump | R | R/W | uint16 | 0 | 1 | 0 | 1 | *1 | ON/OFF | Enable/disable external pump operation, only on Microboosters with valve and no coil (V)
4x0098 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0099 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0100 | I08 HP MWHe | R | R/W | uint16 | 0 | 6553500 | 0 | 65535 | *100 |  | Information is given in manual | 27
4x0101 | I10 HP MWHt | R | R/W | uint16 | 0 | 6553500 | 0 | 65535 | *100 |  | Information is given in manual | 27
4x0102 | I11 EL MWHe | R | R/W | uint16 | 0 | 6553500 | 0 | 65535 | *100 |  | Information is given in manual | 27
4x0103 | I06 Start/Stops | R | R/W | uint16 | 0 | 65535 | 0 | 65535 | *1 |  | Information is given in manual | 27
4x0104 | I01 HP Hours (2 hours) | R | R/W | uint16 | 0 | 65535 | 0 | 65535 | *1 |  | Information is given in manual | 27
4x0105 | I02 EL Hours (2 hours) | R | R/W | uint16 | 0 | 65535 | 0 | 65535 | *1 |  | Information is given in manual | 27
4x0106 | I03 Flow Hours (2 hours) | R | R/W | uint16 | 0 | 65535 | 0 | 65535 | *1 |  | Information is given in manual | 27
4x0107 | BaclupModeRestTime (2 hours) | R | R/W | uint16 | 0 | 65535 | 0 | 65535 | *1 |  | Only for development
4x0108 | HotOnRestTime (2 hours) | R | R/W | uint16 | 0 | 65535 | 0 | 65535 | *1 |  | Only for development
4x0109 | PowerOnCount | R | R/W | uint16 | 0 | 65535 | 0 | 65535 | *1 |  | Only for development
4x0110 | Backup Mode On Time (2 hours) | R | R/W | uint16 | 0 | 65535 | 0 | 65535 | *1 |  | Only for development
4x0111 | Service (2 hours) | R | R/W | uint16 | 0 | 65535 | 0 | 65535 | *1 |  | Information is given in manual | 28
4x0112 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0113 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0114 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0115 | Last Legionelle Date Month | R | R/W | uint16 | 0 | 65535 | 0 | 65535 | *1 |  | Only for development
4x0116 |  | R | R/W | uint16 | 0 | 0 | 0 | 0 | *1
4x0117 | Restart Unit (0=OFF 1=ON) | R | R/W | uint16 | 1 | 1 | 1 | 1 | *1 | ON/OFF | Only for development
4x0118 |  | R | R/W | uint16 | 0 | 65535 | 0 | 65535 | *1
4x0119 |  | R | R/W | uint16 | 0 | 65535 | 0 | 65535 | *1
4x0120 | ErrNoCapacityCnt | [9 empty] | Display error value
4x0121
4x0122 | ErrNoCapacityCntDwn1 | [9 empty] | No capacity counter, -1 every hour
4x0123 | ErrNoCapacityCntDwn2 | [9 empty] | No capacity counter, -1 every hour
4x0124
4x0125
4x0126 | T1_ErrorCnt | [9 empty] | Display error value
4x0127 | T2_ErrorCnt | [9 empty] | Display error value
4x0128 | T3_ErrorCnt | [9 empty] | Display error value
4x0129 | T4_ErrorCnt | [9 empty] | Display error value
4x0130 | T5_ErrorCnt | [9 empty] | Display error value
4x0131 | RressorstatErrorCnt | [9 empty] | Display error value
4x0132 | HotEvapErrorCnt | [9 empty] | Display error value
4x0133 | ColdEvapErrorCnt | [9 empty] | Display error value
4x0134 | HotSourceErrorCnt | [9 empty] | Display error value
4x0135
4x0136
4x0137
4x0138
4x0139
4x0140
4x0141
4x0142
4x0143
4x0144
4x0145
4x0146
4x0147
4x0148
4x0149

## Datapoint (input)
Modbus datapoints P631 | Input register | Microbooster Firmware 1.5 20-05-2021
Modbus Code | Parameter | Data Type | Format | Unit | Comment | Page in manual
3x0000 | ADCvalueCH2 | uint16 | *1 |  | Only for development
3x0001 | ADCvalueCH3 | uint16 | *1 |  | Only for development
3x0002 | ADCvalueCH4 | uint16 | *1 |  | Only for development
3x0003 | ADCvalueCH7 | uint16 | *1 |  | Only for development
3x0004 | ADCvalueCH10 | uint16 | *1 |  | Only for development
3x0005 | ADCvalueCH11 | uint16 | *1 |  | Only for development
3x0006 | ADCvalueCH12 | uint16 | *1 |  | Only for development
3x0007 | ADCvalueCH13 | uint16 | *1 |  | Only for development
3x0008 | ADCvalueCH14 | uint16 | *1 |  | Only for development
3x0009 | ADCvalueCH15 | uint16 | *1 |  | Only for development
3x0010
3x0011 | T1 T source in | int16 | *10 | °C | Information is given in manual | 27
3x0012 | T2 T source out | int16 | *10 | °C | Information is given in manual | 27
3x0013 | T3 T tank | int16 | *10 | °C | Information is given in manual | 27
3x0014 | T4 | int16 | *10 | °C | Not used on Microbooster
3x0015 | T5 | int16 | *10 | °C | Not used on Microbooster
3x0016 | Coil |  |  | ON/OFF | Only for development
3x0017 | Microbooster Mode | uint16 | *1 |  | Information is given in manual | 28/29
3x0018 | ExternalPump | uint16 | *1 | ON/OFF | Only for development
3x0019 | R1 Flow ON | uint16 | *1 | ON/OFF | Information is given in manual | 27
3x0020 | R2 Flow OFF | uint16 | *1 | ON/OFF | Information is given in manual | 27
3x0021 | R3 Coil / External Pump | uint16 | *1 | ON/OFF | Information is given in manual | 27
3x0022 | R4 HP | uint16 | *1 | ON/OFF | Information is given in manual | 27
3x0023 | R5 El Heater | uint16 | *1 | ON/OFF | Information is given in manual | 27
3x0024 | R6 Pressostat | uint16 | *1 | ON/OFF | Information is given in manual | 27
3x0025 | SG1 input | uint16 | *1 | ON/OFF | Information is given in manual | 27
3x0026 | SG2 input | uint16 | *1 | ON/OFF | Information is given in manual | 27
3x0027 | Input V | uint16 | *10 | Volt | Information is given in manual | 27
3x0028 | T avg source in | int16 | *10 | °C | Information is given in manual | 27
3x0029 | T avg source out | int16 | *10 | °C | Information is given in manual | 27
3x0030 | El Power | uint16 | *100 |  | Information is given in manual | 27
3x0031 | W el total | uint16 | *100 |  | Information is given in manual | 27
3x0032 | Heating C | uint16 | *100 |  | Information is given in manual | 27
3x0033 | Water P | uint16 | *100 |  | Information is given in manual | 27
3x0034
3x0035 | T1 Error | uint16 | *1 | ON/OFF | Information is given in manual | 28
3x0036 | T2 Error | uint16 | *1 | ON/OFF | Information is given in manual | 28
3x0037 | T3 Error | uint16 | *1 | ON/OFF | Information is given in manual | 28
3x0038 | T4 Error | uint16 | *1 | ON/OFF | Information is given in manual | 28
3x0039 | T5 Error | uint16 | *1 | ON/OFF | Information is given in manual | 28
3x0040 | HP Error | uint16 | *1 | ON/OFF | Information is given in manual | 28
3x0041 | Hot Evap Error | uint16 | *1 | ON/OFF | Information is given in manual | 28
3x0042 | Cold Evap Error | uint16 | *1 | ON/OFF | Information is given in manual | 28
3x0043 | ModBusError | uint16 | *1 | ON/OFF | Information is given in manual | 28
3x0044 | ServiceError | uint16 | *1 | ON/OFF | Information is given in manual | 28
3x0045 | No Capacity Error | uint16 | *1 | ON/OFF | Information is given in manual | 28
3x0046 | Hot Source T Error | uint16 | *1 | ON/OFF | Information is given in manual | 28
3x0047
3x0048 | HP_OnTemp | int16 | *10 | °C | Temperature to turn on HP
3x0049 | HP_OffTemp | int16 | *10 | °C | Temperature to turn off HP
3x0050 | HP_Released | uint16 | *1 | ON/OFF | Is HP enabled?
3x0051 | E_HeatOnTemp | int16 | *10 | °C | Temperature to turn on heating element
3x0052 | E_HeatOffTemp | int16 | *10 | °C | Temperature to turn off heating element
3x0053 | E_HeatReleasedLevel | uint16 | *1 | ON/OFF | Is heating element enabled?
3x0054 | Cold Mode On | uint16 | *1 | ON/OFF | Only for development
3x0055 | Hot Mode On | uint16 | *1 | ON/OFF | Only for development
3x0056 | HotSourceErrorCnt1 | uint16 | *1 |  | Hot source error count 1, first time within a week
3x0057 | HotSourceErrorCnt2 | uint16 | *1 |  | Hot source error count 2, second time within a week
3x0058 | HotSourceErrorCnt3 | uint16 | *1 |  | Hot source error count 3, third time within a week
3x0059 | Compressor State | uint16 | *1 |  | Only for development
3x0060 | WP_StateTimer | uint16 | *1 | Seconds | Only for development
3x0061 | Source In Last Run | int16 | *10 | °C | Source in last run
3x0062 | CompressorOnTime | uint16 | *1 | Seconds | Compressor on time
3x0063 | Compressor Pause Cnt | uint16 | *1 | Seconds | Compressor pause counter
3x0064 | Mischer position | uint16 | *1 |  | Only for development
3x0065 | Mischer counter | uint16 | *1 | Seconds | Only for development
3x0066 | E74_Delta_T_water | int16 | *10 | °C | Flow handling
3x0067 | E75_Delta_T_water | int16 | *10 | °C | Flow handling
3x0068 | Flow % | uint16 | *1 | % | Flow percentage
3x0069 | R5_ElHeaterOld | uint16 | *1 | ON/OFF | Only for development
3x0070 | HP_ON | uint16 | *1 |  | Heat production present
3x0071
3x0072 | HP_Hours_Sec | uint16 | *1 | Seconds | HP time in seconds
3x0073 | EL_Hours_Sec | uint16 | *1 | Seconds | heating element time in secounds
3x0074 | FlowHours_Sec | uint16 | *1 |  | Flow time in seconds
3x0075 | BaclupModeRestTime_Sec | uint16 | *1 | Seconds | Only for development
3x0076 | HotOnRestTime_Sec | uint16 | *1 | Seconds | Only for development
3x0077 | BackUpModeOnTime_Sec | uint16 | *1 | Seconds | Only for development
3x0078 | FilterOnTime_Sec | uint16 | *1 | Seconds | Only for development
3x0079
3x0080
3x0081 | T1_ErrorCnt | uint16 | *1 | Seconds | T1 error count
3x0082 | T2_ErrorCnt | uint16 | *1 | Seconds | T2 error count
3x0083 | T3_ErrorCnt | uint16 | *1 | Seconds | T3 error count
3x0084 | T4_ErrorCnt | uint16 | *1 | Seconds | T4 error count
3x0085 | T5_ErrorCnt | uint16 | *1 | Seconds | T5 error count
3x0086 | RressorstatErrorCnt | uint16 | *1 | Seconds | Pressostat error count
3x0087 | HotEvapErrorCnt | uint16 | *1 | Seconds | Hot evaporator error count
3x0088 | ColdEvapErrorCnt1 | uint16 | *1 | Seconds | Cold evaporator error count 1, first time within a week
3x0089 | ModBusErrorCnt | uint16 | *1 | Seconds | ModBus error count
3x0090 | NoCapacityErrorCnt | uint16 | *1 |  | No capacity error count
3x0091 | ColdEvapErrorCnt2 | uint16 | *1 |  | Cold evaporator error count 2, second time within a week
3x0092 | BackUpAnswer | uint16 | *1 |  | Allow electrical heating element to continue operation
3x0093 | Errors | uint16 | *1 | Binary | T1_Error Bit0 T2_Error Bit1 T3_Error Bit2 HP_Error Bit5 ColdEvapError Bit6 HotEvapError Bit7 NoCapacityError Bit8 HotSourceTempError Bit9 ServiceError Bit10 ModBusError Bit15 NoCapacityKompressorPause Bit13 NoCapacitySwitchToEheater Bit14
3x0094 | ColdEvapErrorCnt3 | uint16 | *1 |  | Cold evaporator error count 3, third time within a week
3x0095 | T3_TtankOld | int16 | *10 |  | Only for development
3x0096 | Optimal Release HP | uint16 | *1 |  | Only for development
3x0097 | Optimal EL ON | uint16 | *1 |  | Only for development
3x0098 | Legionella State | uint16 | *1 |  | Legionella signal
3x0099 | Low Tarif OnOff | uint16 | *1 |  | Low tarif signal
3x0100 | PV State | uint16 | *1 | Binary | PV signal
3x0101 | SG state | uint16 | *1 |  | SG signal
3x0102
3x0103 | Extern Control State | uint16 | *1 |  | External control
3x0104
3x0105 | Power Fan | uint16 | *1 |  | Fan power estimate
3x0106 | Power Compressor | uint16 | *1 |  | Compressor power estimate
3x0107 | HPWe (Compressor + Fan) | uint16 | *1 |  | HP power estimate
3x0108 | Optimal Qdisp/(Vn*dw*cw) | int16 | *10 |  | Only for development
3x0109 | Optimal Qreq/(Vn*dw*cw) | int16 | *10 |  | Only for development
3x0110
3x0111
3x0112
3x0113
3x0114
3x0115
3x0116 | PassWordOKcntDown | uint16 | *1 | Seconds | Password OK countdown
3x0117
3x0118
3x0119