## Integer Table
Quantity/Functionality | Explanation | Unit | Resolution | Data Type | Access | Register (Hex) | Register (Dec) | Nr of registers | Product Type | Functionality block | Comments
Total Active energy - import |  | kWh | 0.01 | Unsigned | Read | 5000 | 20480 | 4 | D1M 15/20 | Energy value
Total Active energy - export |  | kWh | 0.01 | Unsigned | Read | 5004 | 20484 | 4 | D1M 15/20 | Energy value
Total Active energy - net |  | kWh | 0.01 | Signed | Read | 5008 | 20488 | 4 | D1M 15/20 | Energy value
Total Reactive energy - import |  | kvarh | 0.01 | Unsigned | Read | 500C | 20492 | 4 | D1M 15/20 | Energy value
Total Reactive energy - export |  | kvarh | 0.01 | Unsigned | Read | 5010 | 20496 | 4 | D1M 15/20 | Energy value
Total Reactive energy - net |  | kvarh | 0.01 | Signed | Read | 5014 | 20500 | 4 | D1M 15/20 | Energy value
Total Apparent energy - import |  | kVA | 0.01 | Unsigned | Read | 5018 | 20504 | 4 | D1M 15/20 | Energy value
Total Apparent energy - export |  | kVA | 0.01 | Unsigned | Read | 501C | 20508 | 4 | D1M 15/20 | Energy value
Total Apparent energy - net |  | kVA | 0.01 | Signed | Read | 5020 | 20512 | 4 | D1M 15/20 | Energy value
Total Active energy CO2 - import | Energy * CO2 conversion factor | kg | 0.001 | Unsigned | Read | 5024 | 20516 | 4 | D1M 20 | Energy value
Total Active energy Currency - import | Energy * Currency conversion factor | Currency | 0.001 | Unsigned | Read | 5034 | 20532 | 4 | D1M 20 | Energy value
Total Active energy - import - T 1 | Tariff 1 | kWh | 0.01 | Unsigned | Read | 5170 | 20848 | 4 | D1M 20 | Energy value
Total Active energy - import - T 2 | Tariff 2 | kWh | 0.01 | Unsigned | Read | 5174 | 20852 | 4 | D1M 20 | Energy value
Total Active energy - import - T 3 | Tariff 3 | kWh | 0.01 | Unsigned | Read | 5178 | 20856 | 4 | D1M 20 | Energy value
Total Active energy - import - T 4 | Tariff 4 | kWh | 0.01 | Unsigned | Read | 517C | 20860 | 4 | D1M 20 | Energy value
Total Active energy - export - T 1 | Tariff 1 | kWh | 0.01 | Unsigned | Read | 5190 | 20880 | 4 | D1M 20 | Energy value
Total Active energy - export - T 2 | Tariff 2 | kWh | 0.01 | Unsigned | Read | 5194 | 20884 | 4 | D1M 20 | Energy value
Total Active energy - export - T 3 | Tariff 3 | kWh | 0.01 | Unsigned | Read | 5198 | 20888 | 4 | D1M 20 | Energy value
Total Active energy - export - T 4 | Tariff 4 | kWh | 0.01 | Unsigned | Read | 519C | 20892 | 4 | D1M 20 | Energy value
Total Reactive energy - import - T 1 | Tariff 1 | kvarh | 0.01 | Unsigned | Read | 51B0 | 20912 | 4 | D1M 20 | Energy value
Total Reactive energy - import - T 2 | Tariff 2 | kvarh | 0.01 | Unsigned | Read | 51B4 | 20916 | 4 | D1M 20 | Energy value
Total Reactive energy - import - T 3 | Tariff 3 | kvarh | 0.01 | Unsigned | Read | 51B8 | 20920 | 4 | D1M 20 | Energy value
Total Reactive energy - import - T 4 | Tariff 4 | kvarh | 0.01 | Unsigned | Read | 51BC | 20924 | 4 | D1M 20 | Energy value
Total Reactive energy - export - T 1 | Tariff 1 | kvarh | 0.01 | Unsigned | Read | 51D0 | 20944 | 4 | D1M 20 | Energy value
Total Reactive energy - export - T 2 | Tariff 2 | kvarh | 0.01 | Unsigned | Read | 51D4 | 20948 | 4 | D1M 20 | Energy value
Total Reactive energy - export - T 3 | Tariff 3 | kvarh | 0.01 | Unsigned | Read | 51D8 | 20952 | 4 | D1M 20 | Energy value
Total Reactive energy - export - T 4 | Tariff 4 | kvarh | 0.01 | Unsigned | Read | 51DC | 20956 | 4 | D1M 20 | Energy value
Three phase system voltage | Avg of Line Voltage in 3 phases, equal to Phase Voltage L1 in single phase | V | 0.1 | Unsigned | Read | 5B00 | 23296 | 2 | D1M 15/20 | Real-Time value
Phase voltage L1 | L1 | V | 0.1 | Unsigned | Read | 5B02 | 23298 | 2 | D1M 15/20 | Real-Time value
Phase voltage L2 | L2 | V | 0.1 | Unsigned | Read | 5B04 | 23300 | 2 | D1M 15/20 | Real-Time value
Phase voltage L3 | L3 | V | 0.1 | Unsigned | Read | 5B06 | 23302 | 2 | D1M 15/20 | Real-Time value
Line voltage L1-L2 | L1-L2 | V | 0.1 | Unsigned | Read | 5B08 | 23304 | 2 | D1M 15/20 | Real-Time value
Line voltage L3-L2 | L3-L2 | V | 0.1 | Unsigned | Read | 5B0A | 23306 | 2 | D1M 15/20 | Real-Time value
Line voltage L1-L3 | L1-L3 | V | 0.1 | Unsigned | Read | 5B0C | 23308 | 2 | D1M 15/20 | Real-Time value
Three phase system current | Avg of Current | A | 0.01 | Unsigned | Read | 5B0E | 23310 | 2 | D1M 15/20 | Real-Time value
Current L1 |  | A | 0.01 | Unsigned | Read | 5B10 | 23312 | 2 | D1M 15/20 | Real-Time value
Current L2 |  | A | 0.01 | Unsigned | Read | 5B12 | 23314 | 2 | D1M 15/20 | Real-Time value
Current L3 |  | A | 0.01 | Unsigned | Read | 5B14 | 23316 | 2 | D1M 15/20 | Real-Time value
Current N |  | A | 0.01 | Unsigned | Read | 5B16 | 23318 | 2 | D1M 20 | Real-Time value
Active Power total |  | W | 0.01 | Signed | Read | 5B1A | 23322 | 2 | D1M 15/20 | Real-Time value
Active Power L1 |  | W | 0.01 | Signed | Read | 5B1C | 23324 | 2 | D1M 15/20 | Real-Time value
Active Power L2 |  | W | 0.01 | Signed | Read | 5B1E | 23326 | 2 | D1M 15/20 | Real-Time value
Active power L3 |  | W | 0.01 | Signed | Read | 5B20 | 23328 | 2 | D1M 15/20 | Real-Time value
Reactive Power total |  | var | 0.01 | Signed | Read | 5B22 | 23330 | 2 | D1M 15/20 | Real-Time value
Reactive Power L1 |  | var | 0.01 | Signed | Read | 5B24 | 23332 | 2 | D1M 15/20 | Real-Time value
Reactive Power L2 |  | var | 0.01 | Signed | Read | 5B26 | 23334 | 2 | D1M 15/20 | Real-Time value
Reactive Power L3 |  | var | 0.01 | Signed | Read | 5B28 | 23336 | 2 | D1M 15/20 | Real-Time value
Apparent Power total |  | VA | 0.01 | Signed | Read | 5B2A | 23338 | 2 | D1M 15/20 | Real-Time value
Apparent Power L1 |  | VA | 0.01 | Signed | Read | 5B2C | 23340 | 2 | D1M 15/20 | Real-Time value
Apparent Power L2 |  | VA | 0.01 | Signed | Read | 5B2E | 23342 | 2 | D1M 15/20 | Real-Time value
Apaprent power L3 |  | VA | 0.01 | Signed | Read | 5B30 | 23344 | 2 | D1M 15/20 | Real-Time value
Frequency |  | Hz | 0.01 | Unsigned | Read | 5B32 | 23346 | 1 | D1M 15/20 | Real-Time value
Power Total Angle |  | ° | 0.1 | Signed | Read | 5B33 | 23347 | 1 | D1M 15/20 | Real-Time value
Power Angle L1 |  | ° | 0.1 | Signed | Read | 5B34 | 23348 | 1 | D1M 15/20 | Real-Time value
Power Angle L2 |  | ° | 0.1 | Signed | Read | 5B35 | 23349 | 1 | D1M 15/20 | Real-Time value
Power Angle L3 |  | ° | 0.1 | Signed | Read | 5B36 | 23350 | 1 | D1M 15/20 | Real-Time value
Voltage Angle L1 |  | ° | 0.1 | Signed | Read | 5B37 | 23351 | 1 | D1M 15/20 | Real-Time value
Voltage Angle L2 |  | ° | 0.1 | Signed | Read | 5B38 | 23352 | 1 | D1M 15/20 | Real-Time value
Voltage Angle L3 |  | ° | 0.1 | Signed | Read | 5B39 | 23353 | 1 | D1M 15/20 | Real-Time value
Current Angle L1 |  | ° | 0.1 | Signed | Read | 5B3D | 23357 | 1 | D1M 15/20 | Real-Time value
Current Angle L2 |  | ° | 0.1 | Signed | Read | 5B3E | 23358 | 1 | D1M 15/20 | Real-Time value
Current Angle L3 |  | ° | 0.1 | Signed | Read | 5B3F | 23359 | 1 | D1M 15/20 | Real-Time value
Power factor total |  | -- | 0.001 | Signed | Read | 5B40 | 23360 | 1 | D1M 15/20 | Real-Time value
Power factor L1 |  | -- | 0.001 | Signed | Read | 5B41 | 23361 | 1 | D1M 15/20 | Real-Time value
Power factor L2 |  | -- | 0.001 | Signed | Read | 5B42 | 23362 | 1 | D1M 15/20 | Real-Time value
Power factor L3 |  | -- | 0.001 | Signed | Read | 5B43 | 23363 | 1 | D1M 15/20 | Real-Time value
Cosphi (displacement factor) | Total | ° | 0.001 | Signed | Read | 5B48 | 23368 | 1 | D1M 20 | Real-Time value
Cosphi (displacement factor) | L1 | ° | 0.001 | Signed | Read | 5B49 | 23369 | 1 | D1M 20 | Real-Time value
Cosphi (displacement factor) | L2 | ° | 0.001 | Signed | Read | 5B4A | 23370 | 1 | D1M 20 | Real-Time value
Cosphi (displacement factor) | L3 | ° | 0.001 | Signed | Read | 5B4B | 23371 | 1 | D1M 20 | Real-Time value
Average current L1 | Data value | A | 0.01 | Unsigned | Read | 5BD4 | 23508 | 2 | D1M 20 | Avg/Min/Max value
Average current L2 | Data value | A | 0.01 | Unsigned | Read | 5BD6 | 23510 | 2 | D1M 20 | Avg/Min/Max value
Average current L3 | Data value | A | 0.01 | Unsigned | Read | 5BD8 | 23512 | 2 | D1M 20 | Avg/Min/Max value
Average current neutral | Data value | A | 0.01 | Unsigned | Read | 5BDA | 23514 | 2 | D1M 20 | Avg/Min/Max value
Average voltage L1 | Data value | V | 0.1 | Unsigned | Read | 5BDC | 23516 | 2 | D1M 20 | Avg/Min/Max value
Average voltage L2 | Data value | V | 0.1 | Unsigned | Read | 5BDE | 23518 | 2 | D1M 20 | Avg/Min/Max value
Average voltage L3 | Data value | V | 0.1 | Unsigned | Read | 5BE0 | 23520 | 2 | D1M 20 | Avg/Min/Max value
Average voltage L1-L2 | Data value | V | 0.1 | Unsigned | Read | 5BE2 | 23522 | 2 | D1M 20 | Avg/Min/Max value
Average voltage L2-L3 | Data value | V | 0.1 | Unsigned | Read | 5BE4 | 23524 | 2 | D1M 20 | Avg/Min/Max value
Average voltage L1-L3 | Data value | V | 0.1 | Unsigned | Read | 5BE6 | 23526 | 2 | D1M 20 | Avg/Min/Max value
Average active power total | Data value | W | 0.01 | Signed | Read | 5BE8 | 23528 | 2 | D1M 20 | Avg/Min/Max value
Average active power L1 | Data value | W | 0.01 | Signed | Read | 5BEA | 23530 | 2 | D1M 20 | Avg/Min/Max value
Average active power L2 | Data value | W | 0.01 | Signed | Read | 5BEC | 23532 | 2 | D1M 20 | Avg/Min/Max value
Average active power L3 | Data value | W | 0.01 | Signed | Read | 5BEE | 23534 | 2 | D1M 20 | Avg/Min/Max value
Average reactive power total | Data value | var | 0.01 | Signed | Read | 5BF0 | 23536 | 2 | D1M 20 | Avg/Min/Max value
Average reactive power L1 | Data value | var | 0.01 | Signed | Read | 5BF2 | 23538 | 2 | D1M 20 | Avg/Min/Max value
Average reactive power L2 | Data value | var | 0.01 | Signed | Read | 5BF4 | 23540 | 2 | D1M 20 | Avg/Min/Max value
Average reactive power L3 | Data value | var | 0.01 | Signed | Read | 5BF6 | 23542 | 2 | D1M 20 | Avg/Min/Max value
Average apparent power total | Data value | VA | 0.01 | Signed | Read | 5BF8 | 23544 | 2 | D1M 20 | Avg/Min/Max value
Average apparent power L1 | Data value | VA | 0.01 | Signed | Read | 5BFA | 23546 | 2 | D1M 20 | Avg/Min/Max value
Average apparent power L2 | Data value | VA | 0.01 | Signed | Read | 5BFC | 23548 | 2 | D1M 20 | Avg/Min/Max value
Average apparent power L3 | Data value | VA | 0.01 | Signed | Read | 5BFE | 23550 | 2 | D1M 20 | Avg/Min/Max value
Maximum current L1 | Data value | A | 0.01 | Unsigned | Read | 5C10 | 23568 | 2 | D1M 20 | Avg/Min/Max value
Maximum current L2 | Data value | A | 0.01 | Unsigned | Read | 5C12 | 23570 | 2 | D1M 20 | Avg/Min/Max value
Maximum current L3 | Data value | A | 0.01 | Unsigned | Read | 5C14 | 23572 | 2 | D1M 20 | Avg/Min/Max value
Maximum current neutral | Data value | A | 0.01 | Unsigned | Read | 5C16 | 23574 | 2 | D1M 20 | Avg/Min/Max value
Maximum voltage L1 | Data value | V | 0.1 | Unsigned | Read | 5C18 | 23576 | 2 | D1M 20 | Avg/Min/Max value
Maximum voltage L2 | Data value | V | 0.1 | Unsigned | Read | 5C1A | 23578 | 2 | D1M 20 | Avg/Min/Max value
Maximum voltage L3 | Data value | V | 0.1 | Unsigned | Read | 5C1C | 23580 | 2 | D1M 20 | Avg/Min/Max value
Maximum voltage L1-L2 | Data value | V | 0.1 | Unsigned | Read | 5C1E | 23582 | 2 | D1M 20 | Avg/Min/Max value
Maximum voltage L2-L3 | Data value | V | 0.1 | Unsigned | Read | 5C20 | 23584 | 2 | D1M 20 | Avg/Min/Max value
Maximum voltage L1-L3 | Data value | V | 0.1 | Unsigned | Read | 5C22 | 23586 | 2 | D1M 20 | Avg/Min/Max value
Maximum active power total | Data value | W | 0.01 | Signed | Read | 5C24 | 23588 | 2 | D1M 20 | Avg/Min/Max value
Maximum active power L1 | Data value | W | 0.01 | Signed | Read | 5C26 | 23590 | 2 | D1M 20 | Avg/Min/Max value
Maximum active power L2 | Data value | W | 0.01 | Signed | Read | 5C28 | 23592 | 2 | D1M 20 | Avg/Min/Max value
Maximum active power L3 | Data value | W | 0.01 | Signed | Read | 5C2A | 23594 | 2 | D1M 20 | Avg/Min/Max value
Maximum reactive power total | Data value | var | 0.01 | Signed | Read | 5C2C | 23596 | 2 | D1M 20 | Avg/Min/Max value
Maximum reactive power L1 | Data value | var | 0.01 | Signed | Read | 5C2E | 23598 | 2 | D1M 20 | Avg/Min/Max value
Maximum reactive power L2 | Data value | var | 0.01 | Signed | Read | 5C30 | 23600 | 2 | D1M 20 | Avg/Min/Max value
Maximum reactive power L3 | Data value | var | 0.01 | Signed | Read | 5C32 | 23602 | 2 | D1M 20 | Avg/Min/Max value
Maximum apparent power total | Data value | VA | 0.01 | Signed | Read | 5C34 | 23604 | 2 | D1M 20 | Avg/Min/Max value
Maximum apparent power L1 | Data value | VA | 0.01 | Signed | Read | 5C36 | 23606 | 2 | D1M 20 | Avg/Min/Max value
Maximum apparent power L2 | Data value | VA | 0.01 | Signed | Read | 5C38 | 23608 | 2 | D1M 20 | Avg/Min/Max value
Maximum apparent power L3 | Data value | VA | 0.01 | Signed | Read | 5C3A | 23610 | 2 | D1M 20 | Avg/Min/Max value
Maximum current L1 timestamp | Timestamp (seconds from 2010-01-01) | -- | -- | Unsigned | Read | 5C4C | 23628 | 2 | D1M 20 | Avg/Min/Max value
Maximum current L2 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C4E | 23630 | 2 | D1M 20 | Avg/Min/Max value
Maximum current L3 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C50 | 23632 | 2 | D1M 20 | Avg/Min/Max value
Maximum current neutral timestamp | Timestamp | -- | -- | Unsigned | Read | 5C52 | 23634 | 2 | D1M 20 | Avg/Min/Max value
Maximum voltage L1 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C54 | 23636 | 2 | D1M 20 | Avg/Min/Max value
Maximum voltage L2 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C56 | 23638 | 2 | D1M 20 | Avg/Min/Max value
Maximum voltage L3 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C58 | 23640 | 2 | D1M 20 | Avg/Min/Max value
Maximum voltage L1-L2 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C5A | 23642 | 2 | D1M 20 | Avg/Min/Max value
Maximum voltage L2-L3 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C5C | 23644 | 2 | D1M 20 | Avg/Min/Max value
Maximum voltage L1-L3 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C5E | 23646 | 2 | D1M 20 | Avg/Min/Max value
Maximum active power total timestamp | Timestamp | -- | -- | Unsigned | Read | 5C60 | 23648 | 2 | D1M 20 | Avg/Min/Max value
Maximum active power L1 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C62 | 23650 | 2 | D1M 20 | Avg/Min/Max value
Maximum active power L2 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C64 | 23652 | 2 | D1M 20 | Avg/Min/Max value
Maximum active power L3 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C66 | 23654 | 2 | D1M 20 | Avg/Min/Max value
Maximum reactive power total timestamp | Timestamp | -- | -- | Unsigned | Read | 5C68 | 23656 | 2 | D1M 20 | Avg/Min/Max value
Maximum reactive power L1 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C6A | 23658 | 2 | D1M 20 | Avg/Min/Max value
Maximum reactive power L2 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C6C | 23660 | 2 | D1M 20 | Avg/Min/Max value
Maximum reactive power L3 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C6E | 23662 | 2 | D1M 20 | Avg/Min/Max value
Maximum apparent power total timestamp | Timestamp | -- | -- | Unsigned | Read | 5C70 | 23664 | 2 | D1M 20 | Avg/Min/Max value
Maximum apparent power L1 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C72 | 23666 | 2 | D1M 20 | Avg/Min/Max value
Maximum apparent power L2 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C74 | 23668 | 2 | D1M 20 | Avg/Min/Max value
Maximum apparent power L3 timestamp | Timestamp | -- | -- | Unsigned | Read | 5C76 | 23670 | 2 | D1M 20 | Avg/Min/Max value
Minimum current L1 | Data value | A | 0.01 | Unsigned | Read | 5C88 | 23688 | 2 | D1M 20 | Avg/Min/Max value
Minimum current L2 | Data value | A | 0.01 | Unsigned | Read | 5C8A | 23690 | 2 | D1M 20 | Avg/Min/Max value
Minimum current L3 | Data value | A | 0.01 | Unsigned | Read | 5C8C | 23692 | 2 | D1M 20 | Avg/Min/Max value
Minimum current neutral | Data value | A | 0.01 | Unsigned | Read | 5C8E | 23694 | 2 | D1M 20 | Avg/Min/Max value
Minimum voltage L1 | Data value | V | 0.1 | Unsigned | Read | 5C90 | 23696 | 2 | D1M 20 | Avg/Min/Max value
Minimum voltage L2 | Data value | V | 0.1 | Unsigned | Read | 5C92 | 23698 | 2 | D1M 20 | Avg/Min/Max value
Minimum voltage L3 | Data value | V | 0.1 | Unsigned | Read | 5C94 | 23700 | 2 | D1M 20 | Avg/Min/Max value
Minimum voltage L1-L2 | Data value | V | 0.1 | Unsigned | Read | 5C96 | 23702 | 2 | D1M 20 | Avg/Min/Max value
Minimum voltage L2-L3 | Data value | V | 0.1 | Unsigned | Read | 5C98 | 23704 | 2 | D1M 20 | Avg/Min/Max value
Minimum voltage L1-L3 | Data value | V | 0.1 | Unsigned | Read | 5C9A | 23706 | 2 | D1M 20 | Avg/Min/Max value
Minimum active power total | Data value | W | 0.01 | Signed | Read | 5C9C | 23708 | 2 | D1M 20 | Avg/Min/Max value
Minimum active power L1 | Data value | W | 0.01 | Signed | Read | 5C9E | 23710 | 2 | D1M 20 | Avg/Min/Max value
Minimum active power L2 | Data value | W | 0.01 | Signed | Read | 5CA0 | 23712 | 2 | D1M 20 | Avg/Min/Max value
Minimum active power L3 | Data value | W | 0.01 | Signed | Read | 5CA2 | 23714 | 2 | D1M 20 | Avg/Min/Max value
Minimum reactive power total | Data value | var | 0.01 | Signed | Read | 5CA4 | 23716 | 2 | D1M 20 | Avg/Min/Max value
Minimum reactive power L1 | Data value | var | 0.01 | Signed | Read | 5CA6 | 23718 | 2 | D1M 20 | Avg/Min/Max value
Minimum reactive power L2 | Data value | var | 0.01 | Signed | Read | 5CA8 | 23720 | 2 | D1M 20 | Avg/Min/Max value
Minimum reactive power L3 | Data value | var | 0.01 | Signed | Read | 5CAA | 23722 | 2 | D1M 20 | Avg/Min/Max value
Minimum apparent power total | Data value | VA | 0.01 | Signed | Read | 5CAC | 23724 | 2 | D1M 20 | Avg/Min/Max value
Minimum apparent power L1 | Data value | VA | 0.01 | Signed | Read | 5CAE | 23726 | 2 | D1M 20 | Avg/Min/Max value
Minimum apparent power L2 | Data value | VA | 0.01 | Signed | Read | 5CB0 | 23728 | 2 | D1M 20 | Avg/Min/Max value
Minimum apparent power L3 | Data value | VA | 0.01 | Signed | Read | 5CB2 | 23730 | 2 | D1M 20 | Avg/Min/Max value
Minimum current L1 timestamp | Timestamp (seconds from 2010-01-01) | -- | -- | Unsigned | Read | 5CC4 | 23748 | 2 | D1M 20 | Avg/Min/Max value
Minimum current L2 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CC6 | 23750 | 2 | D1M 20 | Avg/Min/Max value
Minimum current L3 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CC8 | 23752 | 2 | D1M 20 | Avg/Min/Max value
Minimum current neutral timestamp | Timestamp | -- | -- | Unsigned | Read | 5CCA | 23754 | 2 | D1M 20 | Avg/Min/Max value
Minimum voltage L1 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CCC | 23756 | 2 | D1M 20 | Avg/Min/Max value
Minimum voltage L2 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CCE | 23758 | 2 | D1M 20 | Avg/Min/Max value
Minimum voltage L3 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CD0 | 23760 | 2 | D1M 20 | Avg/Min/Max value
Minimum voltage L1-L2 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CD2 | 23762 | 2 | D1M 20 | Avg/Min/Max value
Minimum voltage L2-L3 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CD4 | 23764 | 2 | D1M 20 | Avg/Min/Max value
Minimum voltage L1-L3 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CD6 | 23766 | 2 | D1M 20 | Avg/Min/Max value
Minimum active power total timestamp | Timestamp | -- | -- | Unsigned | Read | 5CD8 | 23768 | 2 | D1M 20 | Avg/Min/Max value
Minimum active power L1 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CDA | 23770 | 2 | D1M 20 | Avg/Min/Max value
Minimum active power L2 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CDC | 23772 | 2 | D1M 20 | Avg/Min/Max value
Minimum active power L3 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CDE | 23774 | 2 | D1M 20 | Avg/Min/Max value
Minimum reactive power total timestamp | Timestamp | -- | -- | Unsigned | Read | 5CE0 | 23776 | 2 | D1M 20 | Avg/Min/Max value
Minimum reactive power L1 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CE2 | 23778 | 2 | D1M 20 | Avg/Min/Max value
Minimum reactive power L2 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CE4 | 23780 | 2 | D1M 20 | Avg/Min/Max value
Minimum reactive power L3 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CE6 | 23782 | 2 | D1M 20 | Avg/Min/Max value
Minimum apparent power total timestamp | Timestamp | -- | -- | Unsigned | Read | 5CE8 | 23784 | 2 | D1M 20 | Avg/Min/Max value
Minimum apparent power L1 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CEA | 23786 | 2 | D1M 20 | Avg/Min/Max value
Minimum apparent power L2 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CEC | 23788 | 2 | D1M 20 | Avg/Min/Max value
Minimum apparent power L3 timestamp | Timestamp | -- | -- | Unsigned | Read | 5CEE | 23790 | 2 | D1M 20 | Avg/Min/Max value
Phase Voltage harmonics | L1 (THD) | % | 0.1 | Unsigned | Read | 5D00 | 23808 | 1 | D1M 20 | Power Quality value
| L1 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 5D01 | 23809 | 39 | D1M 20 | Power Quality value
| L2 (THD) | % | 0.1 | Unsigned | Read | 5D80 | 23936 | 1 | D1M 20 | Power Quality value
| L2 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 5D81 | 23937 | 39 | D1M 20 | Power Quality value
| L3 (THD) | % | 0.1 | Unsigned | Read | 5E00 | 24064 | 1 | D1M 20 | Power Quality value
| L3 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 5E01 | 24065 | 39 | D1M 20 | Power Quality value
Line Voltage harmonics | L1-L2 (THD) | % | 0.1 | Unsigned | Read | 5E80 | 24192 | 1 | D1M 20 | Power Quality value
| L1-L2 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 5E81 | 24193 | 39 | D1M 20 | Power Quality value
| L2-L3 (THD) | % | 0.1 | Unsigned | Read | 5F00 | 24320 | 1 | D1M 20 | Power Quality value
| L2-L3 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 5F01 | 24321 | 39 | D1M 20 | Power Quality value
| L3-L1 (THD) | % | 0.1 | Unsigned | Read | 5F80 | 24448 | 1 | D1M 20 | Power Quality value
| L3-L1 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 5F81 | 24449 | 39 | D1M 20 | Power Quality value
Current harmonics | L1 (THD) | % | 0.1 | Unsigned | Read | 6000 | 24576 | 1 | D1M 20 | Power Quality value
| L1 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 6001 | 24577 | 39 | D1M 20 | Power Quality value
| L2 (THD) | % | 0.1 | Unsigned | Read | 6080 | 24704 | 1 | D1M 20 | Power Quality value
| L2 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 6081 | 24705 | 39 | D1M 20 | Power Quality value
| L3 (THD) | % | 0.1 | Unsigned | Read | 6100 | 24832 | 1 | D1M 20 | Power Quality value
| L3 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 6101 | 24833 | 39 | D1M 20 | Power Quality value
Unbalances | Phase voltage | % | 0.1 | Unsigned | Read | 6200 | 25088 | 2 | D1M 20 | Power Quality value
| Line voltage | % | 0.1 | Unsigned | Read | 6202 | 25090 | 2 | D1M 20 | Power Quality value
| Current | % | 0.1 | Unsigned | Read | 6204 | 25092 | 2 | D1M 20 | Power Quality value
Digital Output 1 | 0=OFF, 1=ON | -- | -- | Unsigned | Read/Write | 6300 | 25344 | 1 | D1M 15/20 | I/O
Digital Output 2 | 0=OFF, 1=ON | -- | -- | Unsigned | Read/Write | 6301 | 25345 | 1 | D1M 15/20 | I/O
Digital Iuput 1 | 0=OFF, 1=ON | -- | -- | Unsigned | Read | 6308 | 25352 | 1 | D1M 20 | I/O
Digital Input 2 | 0=OFF, 1=ON | -- | -- | Unsigned | Read | 6309 | 25353 | 1 | D1M 20 | I/O
Digital Input 1 pulse counter |  | -- | 1 | Unsigned | Read | 6318 | 25368 | 4 | D1M 20 | I/O
Digital Input 2 pulse counter |  | -- | 1 | Unsigned | Read | 631C | 25372 | 4 | D1M 20 | I/O
Digital Input 1 energy | (DI1 pulse counter * DI1 Pulse frequency) | kWh, kvarh, kVA | 0.01 | Unsigned | Read | 6400 | 25600 | 4 | D1M 20 | I/O
Digital Input 2 energy | (DI2 pulse counter * DI2 Pulse frequency) | kWh, kvarh, kVA | 0.01 | Unsigned | Read | 6404 | 25604 | 4 | D1M 20 | I/O
Errors Log | Header - Get next entry, 1=read the next entry | -- | -- | Unsigned | Write | 6500 | 25856 | 1 | D1M 15/20 | Notification
| Header - Entry Number | -- | -- | Unsigned | Read/Write | 6501 | 25857 | 1 | D1M 15/20 | Notification
| Header - Direction, 0=read the entry from most newest 1=read the entry from most oldest | -- | -- | Unsigned | Read/Write | 6507 | 25863 | 1 | D1M 15/20 | Notification
| Header - Total Entry Number | -- | -- | Unsigned | Read | 6508 | 25864 | 1 | D1M 15/20 | Notification
| Data block 1 - Timestamp, 0xYYMMDDHHMMSS | -- | -- | Unsigned | Read | 6510 | 25872 | 3 | D1M 15/20 | Notification
| Data block 1 - Category, 2=Error | -- | -- | Unsigned | Read | 6513 | 25875 | 1 | D1M 15/20 | Notification
| Data block 1 - Error ID, see the sheet "Event ID" | -- | -- | Unsigned | Read | 6514 | 25876 | 1 | D1M 15/20 | Notification
| Data block 1 - Duration, total second of this error | s | -- | Unsigned | Read | 6515 | 25877 | 2 | D1M 15/20 | Notification
| …... | -- | -- | Unsigned | Read | 6517 | 25879 | 3 | D1M 15/20 | Notification
| Data block 15 - Timestamp, 0xYYMMDDHHMMSS | -- | -- | Unsigned | Read | 6572 | 25970 | 3 | D1M 15/20 | Notification
| Data block 15 - Category, 2=Error | -- | -- | Unsigned | Read | 6575 | 25973 | 1 | D1M 15/20 | Notification
| Data block 15 - Error ID, see the sheet "Event ID" | -- | -- | Unsigned | Read | 6576 | 25974 | 1 | D1M 15/20 | Notification
| Data block 15 - Duration, total second of this error | s | -- | Unsigned | Read | 6577 | 25975 | 2 | D1M 15/20 | Notification
Alarms log | Header - Get next entry, 1=read the next entry | -- | -- | Unsigned | Write | 65B0 | 26032 | 1 | D1M 15/20 | Notification
| Header - Entry Number | -- | -- | Unsigned | Read/Write | 65B1 | 26033 | 1 | D1M 15/20 | Notification
| Header - Direction, 0=read the entry from most newest 1=read the entry from most oldest | -- | -- | Unsigned | Read/Write | 65B7 | 26039 | 1 | D1M 15/20 | Notification
| Header - Total Entry Number | -- | -- | Unsigned | Read | 65B8 | 26040 | 1 | D1M 15/20 | Notification
| Data block 1 - Timestamp, 0xYYMMDDHHMMSS | -- | -- | Unsigned | Read | 65C0 | 26048 | 3 | D1M 15/20 | Notification
| Data block 1 - Category, 8=Alarm | -- | -- | Unsigned | Read | 65C3 | 26051 | 1 | D1M 15/20 | Notification
| Data block 1 - Alarm ID, see the sheet "Event ID" | -- | -- | Unsigned | Read | 65C4 | 26052 | 1 | D1M 15/20 | Notification
| Data block 1 - Duration, total second of this alarm | s | -- | Unsigned | Read | 65C5 | 26053 | 2 | D1M 15/20 | Notification
| …... | -- | -- | Unsigned | Read | 65C7 | 26055 | 3 | D1M 15/20 | Notification
| Data block 15 - Timestamp, 0xYYMMDDHHMMSS | -- | -- | Unsigned | Read | 6622 | 26146 | 3 | D1M 15/20 | Notification
| Data block 15 - Category, 8=Alarm | -- | -- | Unsigned | Read | 6625 | 26149 | 1 | D1M 15/20 | Notification
| Data block 15 - Alarm ID, see the sheet "Event ID" | -- | -- | Unsigned | Read | 6626 | 26150 | 1 | D1M 15/20 | Notification
| Data block 15 - Duration, total second of this alarm | s | -- | Unsigned | Read | 6627 | 26151 | 2 | D1M 15/20 | Notification
Audit Log | Header - Get next entry, 1=read the next entry | -- | -- | Unsigned | Write | 6660 | 26208 | 1 | D1M 15/20 | Notification
| Header - Entry Number | -- | -- | Unsigned | Read/Write | 6661 | 26209 | 1 | D1M 15/20 | Notification
| Header - Direction, 0=read the entry from most newest 1=read the entry from most oldest | -- | -- | Unsigned | Read/Write | 6667 | 26215 | 1 | D1M 15/20 | Notification
| Header - Total Entry Number | -- | -- | Unsigned | Read | 6668 | 26216 | 1 | D1M 15/20 | Notification
| Data block - Entry Number | -- | -- | Unsigned | Read | 6670 | 26224 | 2 | D1M 15/20 | Notification
| Data block - Timestamp (seconds from 2010-01-01) | -- | -- | Unsigned | Read | 6672 | 26226 | 2 | D1M 15/20 | Notification
| Data block - Upgrade Counter | -- | -- | Unsigned | Read | 6674 | 26228 | 1 | D1M 15/20 | Notification
| Data block - Firmware Version | -- | -- | ASCII | Read | 6675 | 26229 | 6 | D1M 15/20 | Notification
| Data block - VT Primary | -- | -- | Unsigned | Read | 667B | 26235 | 2 | D1M 15/20 | Notification
| Data block - VT Secondary | -- | -- | Unsigned | Read | 667D | 26237 | 2 | D1M 15/20 | Notification
| Data block - CT Primary | -- | -- | Unsigned | Read | 667F | 26239 | 2 | D1M 15/20 | Notification
| Data block - CT Secondary | -- | -- | Unsigned | Read | 6681 | 26241 | 2 | D1M 15/20 | Notification
| Data block - Type of Network | -- | -- | Unsigned | Read | 6687 | 26247 | 1 | D1M 15/20 | Notification
| Data block - Active energy import Total | kWh | 0.01 | Unsigned | Read | 6688 | 26248 | 4 | D1M 15/20 | Notification
| Data block - Active energy Tariff 1 | kWh | 0.01 | Unsigned | Read | 6698 | 26264 | 4 | D1M 15/20 | Notification
| Data block - Active energy Tariff 2 | kWh | 0.01 | Unsigned | Read | 669C | 26268 | 4 | D1M 15/20 | Notification
| Data block - Active energy Tariff 3 | kWh | 0.01 | Unsigned | Read | 66A0 | 26272 | 4 | D1M 15/20 | Notification
| Data block - Active energy Tariff 4 | kWh | 0.01 | Unsigned | Read | 66A4 | 26276 | 4 | D1M 15/20 | Notification
| Data block - Active energy export Total | kWh | 0.01 | Unsigned | Read | 66B0 | 26288 | 4 | D1M 15/20 | Notification
Warnings log | Header - Get next entry, 1=read the next entry | -- | -- | Unsigned | Write | 6710 | 26384 | 1 | D1M 15/20 | Notification
| Header - Entry Number | -- | -- | Unsigned | Read/Write | 6711 | 26385 | 1 | D1M 15/20 | Notification
| Header - Direction, 0=read the entry from most newest 1=read the entry from most oldest | -- | -- | Unsigned | Read/Write | 6717 | 26391 | 1 | D1M 15/20 | Notification
| Header - Total Entry Number | -- | -- | Unsigned | Read | 6718 | 26392 | 1 | D1M 15/20 | Notification
| Data block 1 - Timestamp, 0xYYMMDDHHMMSS | -- | -- | Unsigned | Read | 6720 | 26400 | 3 | D1M 15/20 | Notification
| Data block 1 - Category, 4=Warning | -- | -- | Unsigned | Read | 6723 | 26403 | 1 | D1M 15/20 | Notification
| Data block 1 - Warning ID, see the sheet "Event ID" | -- | -- | Unsigned | Read | 6724 | 26404 | 1 | D1M 15/20 | Notification
| Data block 1 - Duration, total second of this warning | -- | -- | Unsigned | Read | 6725 | 26405 | 2 | D1M 15/20 | Notification
| …... | -- | -- | Unsigned | Read | 6727 | 26407 | 3 | D1M 15/20 | Notification
| Data block 15 - Timestamp, 0xYYMMDDHHMMSS | -- | -- | Unsigned | Read | 6782 | 26498 | 3 | D1M 15/20 | Notification
| Data block 15 - Category, 4=Warning | -- | -- | Unsigned | Read | 6785 | 26501 | 1 | D1M 15/20 | Notification
| Data block 15 - Warning ID, see the sheet "Event ID" | -- | -- | Unsigned | Read | 6786 | 26502 | 1 | D1M 15/20 | Notification
| Data block 15 - Duration, total second of this warning | -- | -- | Unsigned | Read | 6787 | 26503 | 2 | D1M 15/20 | Notification
Power outage | Header - Get next entry, 1=read the next entry | -- | -- | Unsigned | Write | 67C0 | 26560 | 1 | D1M 15/20 | Notification
| Header - Entry Number | -- | -- | Unsigned | Read/Write | 67C1 | 26561 | 1 | D1M 15/20 | Notification
| Header - Direction, 0=read the entry from most newest 1=read the entry from most oldest | -- | -- | Unsigned | Read/Write | 67C7 | 26567 | 1 | D1M 15/20 | Notification
| Header - Total Entry Number | -- | -- | Unsigned | Read | 67C8 | 26568 | 1 | D1M 15/20 | Notification
| Data block 1 - Timestamp, 0xYYMMDDHHMMSS | -- | -- | Unsigned | Read | 67D0 | 26576 | 3 | D1M 15/20 | Notification
| …... | -- | -- | Unsigned | Read | 67D3 | 26579 | 3 | D1M 15/20 | Notification
| Data block 15 - Timestamp, 0xYYMMDDHHMMSS | -- | -- | Unsigned | Read | 67FA | 26618 | 3 | D1M 15/20 | Notification
Serial number(s) | 10 characters | -- | -- | ASCII | Read | 8900 | 35072 | 5 | D1M 15/20 | Device info
Meter firmware version | "Vx.x.xx Vx.x.xx " = "Main board version +Ethernet board version " | -- | -- | ASCII | Read | 8908 | 35080 | 8 | D1M 15/20 | Device info
Product type number ID | See sheet "Details" | -- | -- | Unsigned | Read | 8910 | 35088 | 1 | D1M 15/20 | Device info
Linear Slave ID | See sheet "Details" | -- | -- | Unsigned | Read | 8911 | 35089 | 1 | D1M 15/20 | Device info
Product tag name | Set by user | -- | -- | ASCII | Read/Write | 8919 | 35097 | 5 | D1M 15/20 | Device info
Type designation | e.g. "D1M 15", "D1M 20" | -- | -- | ASCII | Read | 8960 | 35168 | 6 | D1M 15/20 | Device info
Product Name | e.g. "D1M 20 MODBUS" | -- | -- | ASCII | Read | 8966 | 35174 | 8 | D1M 15/20 | Device info
Date Time | 0xYYMMDDHHMMSS | -- | -- | Unsigned | Read/Write | 8A00 | 35328 | 3 | D1M 20 | Date & Time
Day of week | 1~7, Monday=1, Sunday=7 | -- | -- | Unsigned | Read/Write | 8A03 | 35331 | 1 | D1M 20 | Date & Time
Current tariff | Current active tariff (None, 1~4) |  | -- | Unsigned | Read/Write | 8A07 | 35335 | 1 | D1M 20 | Tariff
Error flags | Bit0 - Error ID 1 status, 1=Error active, 0=Error unactive | -- | -- | Unsigned | Read | 8A13 | 35347 | 4 | D1M 15/20 | Notification
Warning flags | Bit0 - Warning ID 1 status, 1=Warning active, 0=Warning unactive | -- | -- | Unsigned | Read | 8A1F | 35359 | 4 | D1M 15/20 | Notification
Alarm flags | Bit0 - Alarm ID 1 status, 1=Alarm active, 0-Alarm unactive | -- | -- | Unsigned | Read | 8A25 | 35365 | 4 | D1M 15/20 | Notification
Transformer ratios | CT primary | -- | 1 | Unsigned | Read/Write | 8C00 | 35840 | 2 | D1M 15/20 | Installation
| CT secondary | -- | 1 | Unsigned | Read/Write | 8C02 | 35842 | 2 | D1M 15/20 | Installation
| VT primary | -- | 1 | Unsigned | Read/Write | 8C04 | 35844 | 2 | D1M 15/20 | Installation
| VT secondary | -- | 1 | Unsigned | Read/Write | 8C06 | 35846 | 2 | D1M 15/20 | Installation
I/O Port Function configuration | DO1, 0=disable, 2=alarm, 5=pulse output, 6=always ON, 7=always OFF, 8=controlled via communication | -- | -- | Unsigned | Read/Write | 8C0C | 35852 | 1 | D1M 15/20 | I/O
| DO2, same as DO1 | -- | -- | Unsigned | Read/Write | 8C0D | 35853 | 1 | D1M 15/20 | I/O
| DI1, 0=disable, 4=tariff (Read-Only), 5=pulse input | -- | -- | Unsigned | Read/Write | 8C0E | 35854 | 1 | D1M 20 | I/O
| DI2, same as DI1 | -- | -- | Unsigned | Read/Write | 8C0F | 35855 | 1 | D1M 20 | I/O
I/O Port Pulse configuration | I/O Port number, 0=None, 1=DO1, 2=DO2, 256=DI1, 512=DI2 (DI only for D1M20), 32768=LED | -- | -- | Unsigned | Read/Write | 8C10 | 35856 | 1 | D1M 15/20 | I/O
| Type of Energy, 0=None, 1=import PEN total, 2=export PEN total, 3=import QEN total, 4=export QEN total, 5=import SEN total, 6=export SEN total | -- | -- | Unsigned | Read/Write | 8C11 | 35857 | 1 | D1M 15/20 | I/O
| Pulse frequency, 1 ~ 99999999 | Output: imp/MWh, imp/Mvarh Input: Wh/imp, varh/imp | 1 | Unsigned | Read/Write | 8C12 | 35858 | 2 | D1M 15/20 | I/O
| Pulse width, duration time of a entire pulse, 10~990, Don't set this while as DI port. | ms | 1 | Unsigned | Read/Write | 8C14 | 35860 | 2 | D1M 15/20 | I/O
Alarm settings | Alarm number, 1 ~ 15 | -- | -- | Unsigned | Read/Write | 8C60 | 35936 | 1 | D1M 15/20 | Alarm
| Quantity, see the sheet "OBIS Code" | -- | -- | Unsigned | Read/Write | 8C61 | 35937 | 3 | D1M 15/20 | Alarm
| Threshold of Alarm | x | 0.001 | Unsigned | Read/Write | 8C64 | 35940 | 4 | D1M 15/20 | Alarm
| Hysteresis, turn off threshold=threshold – (threshold * hysteresis) | % | 1 | Unsigned | Read/Write | 8C68 | 35944 | 1 | D1M 15/20 | Alarm
| Delays of Alarm | s | 1 | Unsigned | Read/Write | 8C69 | 35945 | 2 | D1M 15/20 | Alarm
| Type of alarm, 1=Cross up, 2=Cross down | -- | -- | Unsigned | Read/Write | 8C6B | 35947 | 1 | D1M 15/20 | Alarm
| Action of enable, 0=Unlog in flash, 1=Log in flash | -- | -- | Unsigned | Read | 8C6C | 35948 | 1 | D1M 15/20 | Alarm
| Link to which DO, 0=None, 1=DO1, 2=DO2 | -- | -- | Unsigned | Read/Write | 8C6D | 35949 | 1 | D1M 15/20 | Alarm
Tariff settings | Tariffs source, 0=RTC, 1=Communication, 2=DI, 0xFF=Disable. | -- | -- | Unsigned | Read/Write | 8C90 | 35984 | 1 | D1M 20 | Tariff
| Input configuration, fixed 0x04E4, see the sheet "Details" | -- | -- | Unsigned | Read | 8C91 | 35985 | 1 | D1M 20 | Tariff
| Weekday type - Monday, 0=weekday, 1=weekend | -- | -- | Unsigned | Read/Write | 8C92 | 35986 | 1 | D1M 20 | Tariff
| Weekday type - Tuesday, 0=weekday, 1=weekend | -- | -- | Unsigned | Read/Write | 8C93 | 35987 | 1 | D1M 20 | Tariff
| Weekday type - Wednesday, 0=weekday, 1=weekend | -- | -- | Unsigned | Read/Write | 8C94 | 35988 | 1 | D1M 20 | Tariff
| Weekday type - Thursday, 0=weekday, 1=weekend | -- | -- | Unsigned | Read/Write | 8C95 | 35989 | 1 | D1M 20 | Tariff
| Weekday type - Friday, 0=weekday, 1=weekend | -- | -- | Unsigned | Read/Write | 8C96 | 35990 | 1 | D1M 20 | Tariff
| Weekday type - Saturday, 0=weekday, 1=weekend | -- | -- | Unsigned | Read/Write | 8C97 | 35991 | 1 | D1M 20 | Tariff
| Weekday type - Sunday, 0=weekday, 1=weekend | -- | -- | Unsigned | Read/Write | 8C98 | 35992 | 1 | D1M 20 | Tariff
| Weekday Start time - T1, 0xHHMM, 0xFFFF: Disable | -- | -- | Unsigned | Read/Write | 8C99 | 35993 | 1 | D1M 20 | Tariff
| Weekday Start time - T2, 0xHHMM | -- | -- | Unsigned | Read/Write | 8C9A | 35994 | 1 | D1M 20 | Tariff
| Weekday Start time - T3, 0xHHMM | -- | -- | Unsigned | Read/Write | 8C9B | 35995 | 1 | D1M 20 | Tariff
| Weekday Start time - T4, 0xHHMM | -- | -- | Unsigned | Read/Write | 8C9C | 35996 | 1 | D1M 20 | Tariff
| Weekend Start time - T1, 0xHHMM, 0xFFFF: Disable | -- | -- | Unsigned | Read/Write | 8CA1 | 36001 | 1 | D1M 20 | Tariff
| Weekend Start time - T2, 0xHHMM | -- | -- | Unsigned | Read/Write | 8CA2 | 36002 | 1 | D1M 20 | Tariff
| Weekend Start time - T3, 0xHHMM | -- | -- | Unsigned | Read/Write | 8CA3 | 36003 | 1 | D1M 20 | Tariff
| Weekend Start time - T4, 0xHHMM | -- | -- | Unsigned | Read/Write | 8CA4 | 36004 | 1 | D1M 20 | Tariff
| Specialday Start time - T1, 0xHHMM, 0xFFFF: Disable | -- | -- | Unsigned | Read/Write | 8CA9 | 36009 | 1 | D1M 20 | Tariff
| Specialday Start time - T2, 0xHHMM | -- | -- | Unsigned | Read/Write | 8CAA | 36010 | 1 | D1M 20 | Tariff
| Specialday Start time - T3, 0xHHMM | -- | -- | Unsigned | Read/Write | 8CAB | 36011 | 1 | D1M 20 | Tariff
| Specialday Start time - T4, 0xHHMM | -- | -- | Unsigned | Read/Write | 8CAC | 36012 | 1 | D1M 20 | Tariff
| Specialday - Total number, 1~50 | -- | -- | Unsigned | Read/Write | 8CD3 | 36051 | 1 | D1M 20 | Tariff
| Specialday - Current special day number, 1~Total number | -- | -- | Unsigned | Read | 8CD4 | 36052 | 1 | D1M 20 | Tariff
| Specialday - Entry Date, 0xYYMMDDxx(xx fixed FF) | -- | -- | Unsigned | Read/Write | 8CD5 | 36053 | 2 | D1M 20 | Tariff
| Specialday - Entry ID, 1~Total number | -- | -- | Unsigned | Read/Write | 8CD7 | 36055 | 1 | D1M 20 | Tariff
Conversion factor of ActIive Energy | CO2, 1 ~ 9999 | kg / kWh | 0.001 | Unsigned | Read/Write | 8CE0 | 36064 | 2 | D1M 20 | Energy Conversion
| Currency, 1 ~ 99999999 | Currency / kWh | 0.001 | Unsigned | Read/Write | 8CE2 | 36066 | 2 | D1M 20 | Energy Conversion
Wires | See the sheet "Details" | -- | -- | Unsigned | Read/Write | 8CE5 | 36069 | 1 | D1M 15/20 | Installation
DST | Start Date time, 0xYYMMDDHH | -- | -- | Unsigned | Read/Write | 8CE6 | 36070 | 2 | D1M 20 | Date & Time
| End Date time, 0xYYMMDDHH | -- | -- | Unsigned | Read/Write | 8CE8 | 36072 | 2 | D1M 20 | Date & Time
| Enable, 0=Disable, 1=Enable | -- | -- | Unsigned | Read/Write | 8CEA | 36074 | 1 | D1M 20 | Date & Time
Modbus RTU | Address, 1~247 | -- | -- | Unsigned | Read/Write | 8CEB | 36075 | 1 | D1M 15/20 | Communication
| Baudrate, 9600~115200 | -- | -- | Unsigned | Read/Write | 8CEC | 36076 | 2 | D1M 15/20 | Communication
| Parity, 0=none, 1=even, 2=odd | -- | -- | Unsigned | Read/Write | 8CEE | 36078 | 1 | D1M 15/20 | Communication
Modbus TCP/IP | DHCP, 0=disable, 1=enable | -- | -- | Unsigned | Read/Write | 8CEF | 36079 | 1 | D1M 20 | Communication
| IP, A.B.C.D=0xAABBCCDD | -- | -- | Unsigned | Read/Write | 8CF0 | 36080 | 2 | D1M 20 | Communication
| Mask, A.B.C.D=0xAABBCCDD | -- | -- | Unsigned | Read/Write | 8CF2 | 36082 | 2 | D1M 20 | Communication
| Gateway, A.B.C.D=0xAABBCCDD | -- | -- | Unsigned | Read/Write | 8CF4 | 36084 | 2 | D1M 20 | Communication
| TCP Port, fixed 502 | -- | -- | Unsigned | Read | 8CF6 | 36086 | 1 | D1M 20 | Communication
Timer up and down | Up Counter | hour | 0.1 | Unsigned | Read | 8CF7 | 36087 | 2 | D1M 20 | Timer
| Down Counter | hour | 0.1 | Unsigned | Read | 8CF9 | 36089 | 2 | D1M 20 | Timer
| Down Counter Reset Value | hour | 0.1 | Unsigned | Read/Write | 8CFB | 36091 | 2 | D1M 20 | Timer
Brightness | 10~100 | % | 1 | Unsigned | Read/Write | 8CFD | 36093 | 1 | D1M 20 | Display
Inactivity time | 1~60 | minute | 1 | Unsigned | Read/Write | 8D00 | 36096 | 1 | D1M 15/20 | Display
Auto scroll time | 5~60 | second | 1 | Unsigned | Read/Write | 8D01 | 36097 | 1 | D1M 15/20 | Display
Home page | See the sheet "Details" | -- | -- | Unsigned | Read/Write | 8D02 | 36098 | 1 | D1M 15/20 | Display
Auto scroll page | See the sheet "Details" | -- | -- | Unsigned | Read/Write | 8D03 | 36099 | 1 | D1M 15/20 | Display
Reset Notification | 1=Reset | -- | -- | Unsigned | Write | 8F57 | 36695 | 1 | D1M 15/20 | Reset
Reset Timer | 1=Reset | -- | -- | Unsigned | Write | 8F59 | 36697 | 1 | D1M 20 | Reset
Reset Energy | 1=Reset | -- | -- | Unsigned | Write | 8F5A | 36698 | 1 | D1M 15/20 | Reset
Reset Factory | 1=Reset | -- | -- | Unsigned | Write | 8F5B | 36699 | 1 | D1M 15/20 | Reset
Reset Max/Min/Average | 1=Reset | -- | -- | Unsigned | Write | 8F5C | 36700 | 1 | D1M 20 | Reset
Reset Global | 1=Reset | -- | -- | Unsigned | Write | 8F5D | 36701 | 1 | D1M 15/20 | Reset
Average time interval | 1~60 | minute | 1 | Unsigned | Read/Write | 8F60 | 36704 | 1 | D1M 20 | Avg/Min/Max
Active power total Scaler 1 |  | W | 1 | Signed | Read | CB1A | 51994 | 2 | D1M 15/20 | Real-Time value
Active power L1 Scaler 1 |  | W | 1 | Signed | Read | CB1C | 51996 | 2 | D1M 15/20 | Real-Time value
Active power L2 Scaler 1 |  | W | 1 | Signed | Read | CB1E | 51998 | 2 | D1M 15/20 | Real-Time value
Active power L3 Scaler 1 |  | W | 1 | Signed | Read | CB20 | 52000 | 2 | D1M 15/20 | Real-Time value
Reactive power total Scaler 1 |  | VAR | 1 | Signed | Read | CB22 | 52002 | 2 | D1M 15/20 | Real-Time value
Reactive power L1 Scaler 1 |  | VAR | 1 | Signed | Read | CB24 | 52004 | 2 | D1M 15/20 | Real-Time value
Reactive power L2 Scaler 1 |  | VAR | 1 | Signed | Read | CB26 | 52006 | 2 | D1M 15/20 | Real-Time value
Reactive power L3 Scaler 1 |  | VAR | 1 | Signed | Read | CB28 | 52008 | 2 | D1M 15/20 | Real-Time value
Apparent power total Scaler 1 |  | VA | 1 | Signed | Read | CB2A | 52010 | 2 | D1M 15/20 | Real-Time value
Apparent power L1 Scaler 1 |  | VA | 1 | Signed | Read | CB2C | 52012 | 2 | D1M 15/20 | Real-Time value
Apparent power L2 Scaler 1 |  | VA | 1 | Signed | Read | CB2E | 52014 | 2 | D1M 15/20 | Real-Time value
Apparent power L3 Scaler 1 |  | VA | 1 | Signed | Read | CB30 | 52016 | 2 | D1M 15/20 | Real-Time value
Average Active power total Scaler 1 |  | W | 1 | Signed | Read | CBE8 | 52200 | 2 | D1M 20 | Avg/Min/Max value
Average Active power L1 Scaler 1 |  | W | 1 | Signed | Read | CBEA | 52202 | 2 | D1M 20 | Avg/Min/Max value
Average Active power L2 Scaler 1 |  | W | 1 | Signed | Read | CBEC | 52204 | 2 | D1M 20 | Avg/Min/Max value
Average Active power L3 Scaler 1 |  | W | 1 | Signed | Read | CBEE | 52206 | 2 | D1M 20 | Avg/Min/Max value
Average Reactive power total Scaler 1 |  | VAR | 1 | Signed | Read | CBF0 | 52208 | 2 | D1M 20 | Avg/Min/Max value
Average Reactive power L1 Scaler 1 |  | VAR | 1 | Signed | Read | CBF2 | 52210 | 2 | D1M 20 | Avg/Min/Max value
Average Reactive power L2 Scaler 1 |  | VAR | 1 | Signed | Read | CBF4 | 52212 | 2 | D1M 20 | Avg/Min/Max value
Average Reactive power L3 Scaler 1 |  | VAR | 1 | Signed | Read | CBF6 | 52214 | 2 | D1M 20 | Avg/Min/Max value
Average Apparent power total Scaler 1 |  | VA | 1 | Signed | Read | CBF8 | 52216 | 2 | D1M 20 | Avg/Min/Max value
Average Apparent power L1 Scaler 1 |  | VA | 1 | Signed | Read | CBFA | 52218 | 2 | D1M 20 | Avg/Min/Max value
Average Apparent power L2 Scaler 1 |  | VA | 1 | Signed | Read | CBFC | 52220 | 2 | D1M 20 | Avg/Min/Max value
Average Apparent power L3 Scaler 1 |  | VA | 1 | Signed | Read | CBFE | 52222 | 2 | D1M 20 | Avg/Min/Max value
Max Active power total Scaler 1 |  | W | 1 | Signed | Read | CC24 | 52260 | 2 | D1M 20 | Avg/Min/Max value
Max Active power L1 Scaler 1 |  | W | 1 | Signed | Read | CC26 | 52262 | 2 | D1M 20 | Avg/Min/Max value
Max Active power L2 Scaler 1 |  | W | 1 | Signed | Read | CC28 | 52264 | 2 | D1M 20 | Avg/Min/Max value
Max Active power L3 Scaler 1 |  | W | 1 | Signed | Read | CC2A | 52266 | 2 | D1M 20 | Avg/Min/Max value
Max Reactive power total Scaler 1 |  | VAR | 1 | Signed | Read | CC2C | 52268 | 2 | D1M 20 | Avg/Min/Max value
Max Reactive power L1 Scaler 1 |  | VAR | 1 | Signed | Read | CC2E | 52270 | 2 | D1M 20 | Avg/Min/Max value
Max Reactive power L2 Scaler 1 |  | VAR | 1 | Signed | Read | CC30 | 52272 | 2 | D1M 20 | Avg/Min/Max value
Max Reactive power L3 Scaler 1 |  | VAR | 1 | Signed | Read | CC32 | 52274 | 2 | D1M 20 | Avg/Min/Max value
Max Apparent power total Scaler 1 |  | VA | 1 | Signed | Read | CC34 | 52276 | 2 | D1M 20 | Avg/Min/Max value
Max Apparent power L1 Scaler 1 |  | VA | 1 | Signed | Read | CC36 | 52278 | 2 | D1M 20 | Avg/Min/Max value
Max Apparent power L2 Scaler 1 |  | VA | 1 | Signed | Read | CC38 | 52280 | 2 | D1M 20 | Avg/Min/Max value
Max Apparent power L3 Scaler 1 |  | VA | 1 | Signed | Read | CC3A | 52282 | 2 | D1M 20 | Avg/Min/Max value
Min Active power total Scaler 1 |  | W | 1 | Signed | Read | CC9C | 52380 | 2 | D1M 20 | Avg/Min/Max value
Min Active power L1 Scaler 1 |  | W | 1 | Signed | Read | CC9E | 52382 | 2 | D1M 20 | Avg/Min/Max value
Min Active power L2 Scaler 1 |  | W | 1 | Signed | Read | CCA0 | 52384 | 2 | D1M 20 | Avg/Min/Max value
Min Active power L3 Scaler 1 |  | W | 1 | Signed | Read | CCA2 | 52386 | 2 | D1M 20 | Avg/Min/Max value
Min Reactive power total Scaler 1 |  | VAR | 1 | Signed | Read | CCA4 | 52388 | 2 | D1M 20 | Avg/Min/Max value
Min Reactive power L1 Scaler 1 |  | VAR | 1 | Signed | Read | CCA6 | 52390 | 2 | D1M 20 | Avg/Min/Max value
Min Reactive power L2 Scaler 1 |  | VAR | 1 | Signed | Read | CCA8 | 52392 | 2 | D1M 20 | Avg/Min/Max value
Min Reactive power L3 Scaler 1 |  | VAR | 1 | Signed | Read | CCAA | 52394 | 2 | D1M 20 | Avg/Min/Max value
Min Apparent power total Scaler 1 |  | VA | 1 | Signed | Read | CCAC | 52396 | 2 | D1M 20 | Avg/Min/Max value
Min Apparent power L1 Scaler 1 |  | VA | 1 | Signed | Read | CCAE | 52398 | 2 | D1M 20 | Avg/Min/Max value
Min Apparent power L2 Scaler 1 |  | VA | 1 | Signed | Read | CCB0 | 52400 | 2 | D1M 20 | Avg/Min/Max value
Min Apparent power L3 Scaler 1 |  | VA | 1 | Signed | Read | CCB2 | 52402 | 2 | D1M 20 | Avg/Min/Max value

## Float Table
Quantity/Functionality | Explanation | Unit | Resolution | Data Type | Access | Register (Hex) | Register (Dec) | Nr of registers | Product Type | Functionality block | Comments
Voltage L1 and Neutral |  | V | 1 | Float 32 bits | Read | 3000 | 12288 | 2 | D1M 15/20 | Real-Time value
Voltage L2 and Neutral |  | V | 1 | Float 32 bits | Read | 3002 | 12290 | 2 | D1M 15/20 | Real-Time value
Voltage L3 and Neutral |  | V | 1 | Float 32 bits | Read | 3004 | 12292 | 2 | D1M 15/20 | Real-Time value
Voltage L1 and L2 |  | V | 1 | Float 32 bits | Read | 3006 | 12294 | 2 | D1M 15/20 | Real-Time value
Voltage L2 and L3 |  | V | 1 | Float 32 bits | Read | 3008 | 12296 | 2 | D1M 15/20 | Real-Time value
Voltage L3 and L1 |  | V | 1 | Float 32 bits | Read | 300A | 12298 | 2 | D1M 15/20 | Real-Time value
Three phase system voltage |  | V | 1 | Float 32 bits | Read | 300C | 12300 | 2 | D1M 15/20 | Real-Time value
Reserved |  |  | 1 | Float 32 bits | Read | 300E | 12302 | 2 |  | Real-Time value
Current phase 1 |  | A | 1 | Float 32 bits | Read | 3010 | 12304 | 2 | D1M 15/20 | Real-Time value
Current phase 2 |  | A | 1 | Float 32 bits | Read | 3012 | 12306 | 2 | D1M 15/20 | Real-Time value
Current phase 3 |  | A | 1 | Float 32 bits | Read | 3014 | 12308 | 2 | D1M 15/20 | Real-Time value
Neutral current |  | A | 1 | Float 32 bits | Read | 3016 | 12310 | 2 | D1M 20 | Real-Time value
Three phase system current |  | A | 1 | Float 32 bits | Read | 3018 | 12312 | 2 | D1M 15/20 | Real-Time value
Reserved |  |  | 1 | Float 32 bits | Read | 301A | 12314 | 2 |  | Real-Time value
Active power phase 1 |  | W | 1 | Float 32 bits | Read | 301C | 12316 | 2 | D1M 15/20 | Real-Time value
Active power phase 2 |  | W | 1 | Float 32 bits | Read | 301E | 12318 | 2 | D1M 15/20 | Real-Time value
Active power phase 3 |  | W | 1 | Float 32 bits | Read | 3020 | 12320 | 2 | D1M 15/20 | Real-Time value
Active power total |  | W | 1 | Float 32 bits | Read | 3022 | 12322 | 2 | D1M 15/20 | Real-Time value
Reactive power phase 1 |  | Var | 1 | Float 32 bits | Read | 3024 | 12324 | 2 | D1M 15/20 | Real-Time value
Reactive power phase 2 |  | Var | 1 | Float 32 bits | Read | 3026 | 12326 | 2 | D1M 15/20 | Real-Time value
Reactive power phase 3 |  | Var | 1 | Float 32 bits | Read | 3028 | 12328 | 2 | D1M 15/20 | Real-Time value
Reactive power total |  | Var | 1 | Float 32 bits | Read | 302A | 12330 | 2 | D1M 15/20 | Real-Time value
Apparente power fase 1 |  | VA | 1 | Float 32 bits | Read | 302C | 12332 | 2 | D1M 15/20 | Real-Time value
Apparente power fase 2 |  | VA | 1 | Float 32 bits | Read | 302E | 12334 | 2 | D1M 15/20 | Real-Time value
Apparente power fase 3 |  | VA | 1 | Float 32 bits | Read | 3030 | 12336 | 2 | D1M 15/20 | Real-Time value
Apparente power total |  | VA | 1 | Float 32 bits | Read | 3032 | 12338 | 2 | D1M 15/20 | Real-Time value
Reserved |  |  | 1 | Float 32 bits | Read | 3034 | 12340 | 2 | D1M 15/20 | Real-Time value
Power factor phase 1 |  |  | 1 | Float 32 bits | Read | 3036 | 12342 | 2 | D1M 15/20 | Power Quality value
Power factor phase 2 |  |  | 1 | Float 32 bits | Read | 3038 | 12344 | 2 | D1M 15/20 | Power Quality value
Power factor phase 3 |  |  | 1 | Float 32 bits | Read | 303A | 12346 | 2 | D1M 15/20 | Power Quality value
Power factor phase total |  |  | 1 | Float 32 bits | Read | 303C | 12348 | 2 | D1M 15/20 | Power Quality value
Displacement factor phase 1 |  |  | 1 | Float 32 bits | Read | 303E | 12350 | 2 | D1M 15/20 | Power Quality value
Displacement factor phase 2 |  |  | 1 | Float 32 bits | Read | 3040 | 12352 | 2 | D1M 15/20 | Power Quality value
Displacement factor phase 3 |  |  | 1 | Float 32 bits | Read | 3042 | 12354 | 2 | D1M 15/20 | Power Quality value
Displacement factor phase total |  |  | 1 | Float 32 bits | Read | 3044 | 12356 | 2 | D1M 15/20 | Power Quality value
Angle Phi1 |  | ° | 1 | Float 32 bits | Read | 3046 | 12358 | 2 | D1M 15/20 | Real-Time value
Angle Phi2 |  | ° | 1 | Float 32 bits | Read | 3048 | 12360 | 2 | D1M 15/20 | Real-Time value
Angle Phi3 |  | ° | 1 | Float 32 bits | Read | 304A | 12362 | 2 | D1M 15/20 | Real-Time value
Angle Phi total |  | ° | 1 | Float 32 bits | Read | 304C | 12364 | 2 | D1M 15/20 | Real-Time value
Frequency |  | Hz | 1 | Float 32 bits | Read | 304E | 12366 | 2 | D1M 15/20 | Real-Time value
Reserved |  |  | 1 | Float 32 bits | Read | 3050 | 12368 | 12 |  | Real-Time value
Voltage angle phase 1 |  | ° | 1 | Float 32 bits | Read | 305C | 12380 | 2 | D1M 15/20 | Real-Time value
Voltage angle phase 2 |  | ° | 1 | Float 32 bits | Read | 305E | 12382 | 2 | D1M 15/20 | Real-Time value
Voltage angle phase 3 |  | ° | 1 | Float 32 bits | Read | 3060 | 12384 | 2 | D1M 15/20 | Real-Time value
Currente angle phase 1 |  | ° | 1 | Float 32 bits | Read | 3062 | 12386 | 2 | D1M 15/20 | Real-Time value
Currente angle phase 2 |  | ° | 1 | Float 32 bits | Read | 3064 | 12388 | 2 | D1M 15/20 | Real-Time value
Currente angle phase 3 |  | ° | 1 | Float 32 bits | Read | 3066 | 12390 | 2 | D1M 15/20 | Real-Time value
THD Phase voltage 1 |  | % | 1 | Float 32 bits | Read | 3068 | 12392 | 2 | D1M 20 | Power Quality value
THD Phase voltage 2 |  | % | 1 | Float 32 bits | Read | 306A | 12394 | 2 | D1M 20 | Power Quality value
THD Phase voltage 3 |  | % | 1 | Float 32 bits | Read | 306C | 12396 | 2 | D1M 20 | Power Quality value
THD Current 1 |  | % | 1 | Float 32 bits | Read | 306E | 12398 | 2 | D1M 20 | Power Quality value
THD Current 2 |  | % | 1 | Float 32 bits | Read | 3070 | 12400 | 2 | D1M 20 | Power Quality value
THD Current 3 |  | % | 1 | Float 32 bits | Read | 3072 | 12402 | 2 | D1M 20 | Power Quality value
Umbalance phase voltage |  | % | 1 | Float 32 bits | Read | 3074 | 12404 | 2 | D1M 20 | Power Quality value
Umbalance line voltage |  | % | 1 | Float 32 bits | Read | 3076 | 12406 | 2 | D1M 20 | Power Quality value
Umbalance currente |  | % | 1 | Float 32 bits | Read | 3078 | 12408 | 2 | D1M 20 | Power Quality value
Reserved |  |  | 1 | Float 32 bits | Read | 307A | 12410 | 10 |  | Power Quality value
Average Voltage L1 and Neutral |  | V | 1 | Float 32 bits | Read | 3084 | 12420 | 2 | D1M 20 | Avg/Min/Max value
Average Voltage L2 and Neutral |  | V | 1 | Float 32 bits | Read | 3086 | 12422 | 2 | D1M 20 | Avg/Min/Max value
Average Voltage L3 and Neutral |  | V | 1 | Float 32 bits | Read | 3088 | 12424 | 2 | D1M 20 | Avg/Min/Max value
Average Voltage L1 and L2 |  | V | 1 | Float 32 bits | Read | 308A | 12426 | 2 | D1M 20 | Avg/Min/Max value
Average Voltage L2 and L3 |  | V | 1 | Float 32 bits | Read | 308C | 12428 | 2 | D1M 20 | Avg/Min/Max value
Average Voltage L3 and L1 |  | V | 1 | Float 32 bits | Read | 308E | 12430 | 2 | D1M 20 | Avg/Min/Max value
Average Current phase 1 |  | A | 1 | Float 32 bits | Read | 3090 | 12432 | 2 | D1M 20 | Avg/Min/Max value
Average Current phase 2 |  | A | 1 | Float 32 bits | Read | 3092 | 12434 | 2 | D1M 20 | Avg/Min/Max value
Average Current phase 3 |  | A | 1 | Float 32 bits | Read | 3094 | 12436 | 2 | D1M 20 | Avg/Min/Max value
Average Neutral current |  | A | 1 | Float 32 bits | Read | 3096 | 12438 | 2 | D1M 20 | Avg/Min/Max value
Average Active power phase 1 |  | W | 1 | Float 32 bits | Read | 3098 | 12440 | 2 | D1M 20 | Avg/Min/Max value
Average Active power phase 2 |  | W | 1 | Float 32 bits | Read | 309A | 12442 | 2 | D1M 20 | Avg/Min/Max value
Average Active power phase 3 |  | W | 1 | Float 32 bits | Read | 309C | 12444 | 2 | D1M 20 | Avg/Min/Max value
Average Active power total |  | W | 1 | Float 32 bits | Read | 309E | 12446 | 2 | D1M 20 | Avg/Min/Max value
Average Reactive power phase 1 |  | Var | 1 | Float 32 bits | Read | 30A0 | 12448 | 2 | D1M 20 | Avg/Min/Max value
Average Reactive power phase 2 |  | Var | 1 | Float 32 bits | Read | 30A2 | 12450 | 2 | D1M 20 | Avg/Min/Max value
Average Reactive power phase 3 |  | Var | 1 | Float 32 bits | Read | 30A4 | 12452 | 2 | D1M 20 | Avg/Min/Max value
Average Reactive power total |  | Var | 1 | Float 32 bits | Read | 30A6 | 12454 | 2 | D1M 20 | Avg/Min/Max value
Average Apparente power fase 1 |  | VA | 1 | Float 32 bits | Read | 30A8 | 12456 | 2 | D1M 20 | Avg/Min/Max value
Average Apparente power fase 2 |  | VA | 1 | Float 32 bits | Read | 30AA | 12458 | 2 | D1M 20 | Avg/Min/Max value
Average Apparente power fase 3 |  | VA | 1 | Float 32 bits | Read | 30AC | 12460 | 2 | D1M 20 | Avg/Min/Max value
Average Apparente power total |  | VA | 1 | Float 32 bits | Read | 30AE | 12462 | 2 | D1M 20 | Avg/Min/Max value
Maximum Voltage L1 and Neutral |  | V | 1 | Float 32 bits | Read | 30B0 | 12464 | 2 | D1M 20 | Avg/Min/Max value
Maximum Voltage L2 and Neutral |  | V | 1 | Float 32 bits | Read | 30B2 | 12466 | 2 | D1M 20 | Avg/Min/Max value
Maximum Voltage L3 and Neutral |  | V | 1 | Float 32 bits | Read | 30B4 | 12468 | 2 | D1M 20 | Avg/Min/Max value
Maximum Voltage L1 and L2 |  | V | 1 | Float 32 bits | Read | 30B6 | 12470 | 2 | D1M 20 | Avg/Min/Max value
Maximum Voltage L2 and L3 |  | V | 1 | Float 32 bits | Read | 30B8 | 12472 | 2 | D1M 20 | Avg/Min/Max value
Maximum Voltage L3 and L1 |  | V | 1 | Float 32 bits | Read | 30BA | 12474 | 2 | D1M 20 | Avg/Min/Max value
Maximum Current phase 1 |  | A | 1 | Float 32 bits | Read | 30BC | 12476 | 2 | D1M 20 | Avg/Min/Max value
Maximum Current phase 2 |  | A | 1 | Float 32 bits | Read | 30BE | 12478 | 2 | D1M 20 | Avg/Min/Max value
Maximum Current phase 3 |  | A | 1 | Float 32 bits | Read | 30C0 | 12480 | 2 | D1M 20 | Avg/Min/Max value
Maximum Neutral current |  | A | 1 | Float 32 bits | Read | 30C2 | 12482 | 2 | D1M 20 | Avg/Min/Max value
Maximum Active power phase 1 |  | W | 1 | Float 32 bits | Read | 30C4 | 12484 | 2 | D1M 20 | Avg/Min/Max value
Maximum Active power phase 2 |  | W | 1 | Float 32 bits | Read | 30C6 | 12486 | 2 | D1M 20 | Avg/Min/Max value
Maximum Active power phase 3 |  | W | 1 | Float 32 bits | Read | 30C8 | 12488 | 2 | D1M 20 | Avg/Min/Max value
Maximum Active power total |  | W | 1 | Float 32 bits | Read | 30CA | 12490 | 2 | D1M 20 | Avg/Min/Max value
Maximum Reactive power phase 1 |  | Var | 1 | Float 32 bits | Read | 30CC | 12492 | 2 | D1M 20 | Avg/Min/Max value
Maximum Reactive power phase 2 |  | Var | 1 | Float 32 bits | Read | 30CE | 12494 | 2 | D1M 20 | Avg/Min/Max value
Maximum Reactive power phase 3 |  | Var | 1 | Float 32 bits | Read | 30D0 | 12496 | 2 | D1M 20 | Avg/Min/Max value
Maximum Reactive power total |  | Var | 1 | Float 32 bits | Read | 30D2 | 12498 | 2 | D1M 20 | Avg/Min/Max value
Maximum Apparente power fase 1 |  | VA | 1 | Float 32 bits | Read | 30D4 | 12500 | 2 | D1M 20 | Avg/Min/Max value
Maximum Apparente power fase 2 |  | VA | 1 | Float 32 bits | Read | 30D6 | 12502 | 2 | D1M 20 | Avg/Min/Max value
Maximum Apparente power fase 3 |  | VA | 1 | Float 32 bits | Read | 30D8 | 12504 | 2 | D1M 20 | Avg/Min/Max value
Maximum Apparente power total |  | VA | 1 | Float 32 bits | Read | 30DA | 12506 | 2 | D1M 20 | Avg/Min/Max value
Minimum Voltage L1 and Neutral |  | V | 1 | Float 32 bits | Read | 30DC | 12508 | 2 | D1M 20 | Avg/Min/Max value
Minimum Voltage L2 and Neutral |  | V | 1 | Float 32 bits | Read | 30DE | 12510 | 2 | D1M 20 | Avg/Min/Max value
Minimum Voltage L3 and Neutral |  | V | 1 | Float 32 bits | Read | 30E0 | 12512 | 2 | D1M 20 | Avg/Min/Max value
Minimum Voltage L1 and L2 |  | V | 1 | Float 32 bits | Read | 30E2 | 12514 | 2 | D1M 20 | Avg/Min/Max value
Minimum Voltage L2 and L3 |  | V | 1 | Float 32 bits | Read | 30E4 | 12516 | 2 | D1M 20 | Avg/Min/Max value
Minimum Voltage L3 and L1 |  | V | 1 | Float 32 bits | Read | 30E6 | 12518 | 2 | D1M 20 | Avg/Min/Max value
Minimum Current phase 1 |  | A | 1 | Float 32 bits | Read | 30E8 | 12520 | 2 | D1M 20 | Avg/Min/Max value
Minimum Current phase 2 |  | A | 1 | Float 32 bits | Read | 30EA | 12522 | 2 | D1M 20 | Avg/Min/Max value
Minimum Current phase 3 |  | A | 1 | Float 32 bits | Read | 30EC | 12524 | 2 | D1M 20 | Avg/Min/Max value
Minimum Neutral current |  | A | 1 | Float 32 bits | Read | 30EE | 12526 | 2 | D1M 20 | Avg/Min/Max value
Minimum Active power phase 1 |  | W | 1 | Float 32 bits | Read | 30F0 | 12528 | 2 | D1M 20 | Avg/Min/Max value
Minimum Active power phase 2 |  | W | 1 | Float 32 bits | Read | 30F2 | 12530 | 2 | D1M 20 | Avg/Min/Max value
Minimum Active power phase 3 |  | W | 1 | Float 32 bits | Read | 30F4 | 12532 | 2 | D1M 20 | Avg/Min/Max value
Minimum Active power total |  | W | 1 | Float 32 bits | Read | 30F6 | 12534 | 2 | D1M 20 | Avg/Min/Max value
Minimum Reactive power phase 1 |  | Var | 1 | Float 32 bits | Read | 30F8 | 12536 | 2 | D1M 20 | Avg/Min/Max value
Minimum Reactive power phase 2 |  | Var | 1 | Float 32 bits | Read | 30FA | 12538 | 2 | D1M 20 | Avg/Min/Max value
Minimum Reactive power phase 3 |  | Var | 1 | Float 32 bits | Read | 30FC | 12540 | 2 | D1M 20 | Avg/Min/Max value
Minimum Reactive power total |  | Var | 1 | Float 32 bits | Read | 30FE | 12542 | 2 | D1M 20 | Avg/Min/Max value
Minimum Apparente power fase 1 |  | VA | 1 | Float 32 bits | Read | 3100 | 12544 | 2 | D1M 20 | Avg/Min/Max value
Minimum Apparente power fase 2 |  | VA | 1 | Float 32 bits | Read | 3102 | 12546 | 2 | D1M 20 | Avg/Min/Max value
Minimum Apparente power fase 3 |  | VA | 1 | Float 32 bits | Read | 3104 | 12548 | 2 | D1M 20 | Avg/Min/Max value
Minimum Apparente power total |  | VA | 1 | Float 32 bits | Read | 3106 | 12550 | 2 | D1M 20 | Avg/Min/Max value
Reserved |  |  | 1 | Float 32 bits | Read | 3108 | 12552 | 2 |  | Avg/Min/Max value
THD Line voltage 1 |  | % | 1 | Float 32 bits | Read | 310A | 12554 | 2 | D1M 20 | Power Quality value
THD Line voltage 2 |  | % | 1 | Float 32 bits | Read | 310C | 12556 | 2 | D1M 20 | Power Quality value
THD Line voltage 3 |  | % | 1 | Float 32 bits | Read | 310E | 12558 | 2 | D1M 20 | Power Quality value
Total Active energy - import |  | kWh | 1 | Float 32 bits | Read | 3110 | 12560 | 2 | D1M 15/20 | Energy value
Total Active energy - export |  | kWh | 1 | Float 32 bits | Read | 3112 | 12562 | 2 | D1M 15/20 | Energy value
Total Active energy - net |  | kWh | 1 | Float 32 bits | Read | 3114 | 12564 | 2 | D1M 15/20 | Energy value
Total Reactive energy - import |  | kvarh | 1 | Float 32 bits | Read | 3116 | 12566 | 2 | D1M 15/20 | Energy value
Total Reactive energy - export |  | kvarh | 1 | Float 32 bits | Read | 3118 | 12568 | 2 | D1M 15/20 | Energy value
Total Reactive energy - net |  | kvarh | 1 | Float 32 bits | Read | 311A | 12570 | 2 | D1M 15/20 | Energy value
Total Apparent energy - import |  | kVA | 1 | Float 32 bits | Read | 311C | 12572 | 2 | D1M 15/20 | Energy value
Total Apparent energy - export |  | kVA | 1 | Float 32 bits | Read | 311E | 12574 | 2 | D1M 15/20 | Energy value
Total Apparent energy - net |  | kVA | 1 | Float 32 bits | Read | 3120 | 12576 | 2 | D1M 15/20 | Energy value
Total Active energy CO2 - import |  | kg | 1 | Float 32 bits | Read | 3122 | 12578 | 2 | D1M 20 | Energy value
Total Active energy Currency - import |  | Currency | 1 | Float 32 bits | Read | 3124 | 12580 | 2 | D1M 20 | Energy value
Total Active energy - import T1 | Tariff 1 | kWh | 1 | Float 32 bits | Read | 3126 | 12582 | 2 | D1M 20 | Energy value
Total Active energy - import T2 | Tariff 2 | kWh | 1 | Float 32 bits | Read | 3128 | 12584 | 2 | D1M 20 | Energy value
Total Active energy - import T3 | Tariff 3 | kWh | 1 | Float 32 bits | Read | 312A | 12586 | 2 | D1M 20 | Energy value
Total Active energy - import T4 | Tariff 4 | kWh | 1 | Float 32 bits | Read | 312C | 12588 | 2 | D1M 20 | Energy value
Total Active energy - export T1 | Tariff 1 | kWh | 1 | Float 32 bits | Read | 312E | 12590 | 2 | D1M 20 | Energy value
Total Active energy - export T2 | Tariff 2 | kWh | 1 | Float 32 bits | Read | 3130 | 12592 | 2 | D1M 20 | Energy value
Total Active energy - export T3 | Tariff 3 | kWh | 1 | Float 32 bits | Read | 3132 | 12594 | 2 | D1M 20 | Energy value
Total Active energy - export T4 | Tariff 4 | kWh | 1 | Float 32 bits | Read | 3134 | 12596 | 2 | D1M 20 | Energy value
Total Reactive energy - import T1 | Tariff 1 | kvarh | 1 | Float 32 bits | Read | 3136 | 12598 | 2 | D1M 20 | Energy value
Total Reactive energy - import T2 | Tariff 2 | kvarh | 1 | Float 32 bits | Read | 3138 | 12600 | 2 | D1M 20 | Energy value
Total Reactive energy - import T3 | Tariff 3 | kvarh | 1 | Float 32 bits | Read | 313A | 12602 | 2 | D1M 20 | Energy value
Total Reactive energy - import T4 | Tariff 4 | kvarh | 1 | Float 32 bits | Read | 313C | 12604 | 2 | D1M 20 | Energy value
Total Reactive energy - export T1 | Tariff 1 | kvarh | 1 | Float 32 bits | Read | 313E | 12606 | 2 | D1M 20 | Energy value
Total Reactive energy - export T2 | Tariff 2 | kvarh | 1 | Float 32 bits | Read | 3140 | 12608 | 2 | D1M 20 | Energy value
Total Reactive energy - export T3 | Tariff 3 | kvarh | 1 | Float 32 bits | Read | 3142 | 12610 | 2 | D1M 20 | Energy value
Total Reactive energy - export T4 | Tariff 4 | kvarh | 1 | Float 32 bits | Read | 3144 | 12612 | 2 | D1M 20 | Energy value

## Details
Product type | D1M 15 | D1M 15 Modbus | D1M 20 Modbus | D1M 20 Ethernet
Linear SlaveID | 403 | 404 | 405 | 405
Secondary SlaveID | 147 | 148 | 149 | 149
PID | 440 | 441 | 442 | 443
Wires | 3 phase-4 wires network+3CTs (3N3T) | 3 phase-4 wires network+1CT (3N1T) | 3 phase-3 wires network+3CTs (3 3T) | 3 phase-3 wires network+2CTs (3 2T) | 3 phase-3 wires network+1CT (3 1T) | 2 phase-3 wires network+2CTs (2N2T) | 2 phase-2 wires network+1CT (1N1T)
| 1 | 2 | 3 | 4 | 5 | 6 | 7
11H Function code | Format | Part 1 | Part 2 | Part 3 | Part 4 | Part 5 | Part 6 | Part 7
| Byte count | 1 | 1 | 2 | 2 | 16 | 2 | 1
| Describe | SlaveID MS Byte | Run Indicator Status | Firmware Major Ver | Event Addr | SN Code(ASCII Big Endian) If less than 16 add Null | Field code and length | Secondary SlaveID
| Example | 0xFA(Fixed) | 0xFF(Fixed) | 0x0109 | 0xFFFF(Fixed) | T012345678 | 0x0201(Fixed) | 0x45
V1.9
|  |  | 8 bits | 8 bits
|  |  | 15~08 bit | 07~00 bit
|  |  | Major Version | Minor Version
I/O ports function | possible value | Functionality | Observation
| 0 | Disabled
| 1 | IO | For inputs
| 2 | Alarm | The I/O will be defined during alarm setting.
| 3 | Complex alarm
| 4 | Tariff
| 5 | Pulse | The I/O will be defined during pulse setting.
| 6 | Always on
| 7 | Always off
| 8 | Communication
Tariff Input configuration | Byte | Bits | Description | Possible values
| 0 (high byte) | Entire byte | The number of tariffs to use | 1-4
| 1 (low byte) | 0-1 | Tariff to activate when both inputs are OFF | 0-3 (0 = tariff 1, etc)
|  | 2-3 | Tariff to activate when input 1 is ON and input 2 is OFF | 0-3 (0 = tariff 1, etc)
|  | 4-5 | Tariff to activate when input 1 is OFF and input 2 is ON | 0-3 (0 = tariff 1, etc)
|  | 6-7 | Tariff to activate when both inputs are ON | 0-3 (0 = tariff 1, etc)
HOME page | Options | Value
| Summary page | 0
| Phase voltage page | 1
| Line voltage page | 2
| Current page | 3
Auto scroll page | Options | Value
| None | 0
| All realtime measurement pages | 1
| phasetotal of Home page except for Summary | 2

## OBIS Code
Parameter | OBIS Code | Column1 | Comment
QUANTITY IDENTIFIERS MONITORED BY ALARMS: |  | Alarm threshold range
Voltage L1 | 1.0.32.7.0.255 | 0-(750*120%)kV | OBIS use 3 registers (i.e. 6 bytes) to discribe each qutities. Eg. 1.0.32.7.0.255 equal to 0x0100200700FF
Voltage L2 | 1.0.52.7.0.255 | 0-(750*120%)kV
Voltage L3 | 1.0.72.7.0.255 | 0-(750*120%)kV
Voltage L1-L2 | 1.0.134.7.0.255 | 0-(750*√3*120%)kV
Voltage L2-L3 | 1.0.135.7.0.255 | 0-(750*√3*120%)kV
Voltage L1-L3 | 1.0.136.7.0.255 | 0-(750*√3*120%)kV
Current L1 | 1.0.31.7.0.255 | 0-(50*120%)kA
Current L2 | 1.0.51.7.0.255 | 0-(50*120%)kA
Current L3 | 1.0.71.7.0.255 | 0-(50*120%)kA
Current N | 1.0.91.7.0.255 | 0-(50*120%)kA
Active power total | 1.0.16.7.0.255 | 0-9999MW
Active power L1 | 1.0.36.7.0.255 | 0-9999MW
Active power L2 | 1.0.56.7.0.255 | 0-9999MW
Active power L3 | 1.0.76.7.0.255 | 0-9999MW
Rective power total | 1.0.128.7.0.255 | 0-9999Mvar
Rective power L1 | 1.0.129.7.0.255 | 0-9999Mvar
Rective power L2 | 1.0.130.7.0.255 | 0-9999Mvar
Rective power L3 | 1.0.131.7.0.255 | 0-9999Mvar
Apparent power total | 1.0.137.7.0.255 | 0-9999MVA
Apparent power L1 | 1.0.138.7.0.255 | 0-9999MVA
Apparent power L2 | 1.0.139.7.0.255 | 0-9999MVA
Apparent power L3 | 1.0.140.7.0.255 | 0-9999MVA
Power factor total | 1.0.13.7.0.255 | 0-0.999
Power factor L1 | 1.0.33.7.0.255 | 0-0.999
Power factor L2 | 1.0.53.7.0.255 | 0-0.999
Power factor L3 | 1.0.73.7.0.255 | 0-0.999
THD voltage L1 | 1.0.32.7.124.255 | 0-99,9%
THD voltage L2 | 1.0.52.7.124.255 | 0-99,9%
THD voltage L3 | 1.0.72.7.124.255 | 0-99,9%
THD voltage L1-L2 | 1.0.134.7.124.255 | 0-99,9%
THD voltage L2-L3 | 1.0.135.7.124.255 | 0-99,9%
THD voltage L1-L3 | 1.0.136.7.124.255 | 0-99,9%
THD current L1 | 1.0.31.7.124.255 | 0-99,9%
THD current L2 | 1.0.51.7.124.255 | 0-99,9%
THD current L3 | 1.0.71.7.124.255 | 0-99,9%
Frequency | 1.0.14.7.0.255 | 0-70Hz

## Event ID
Event ID for notifications (Errors, Alarms and Warnings)
Number | Error ID | Description
1 | 40 | Audit log error, space full
2 | 42 | Persistent storage error, EEPROM chip
3 | 43 | RAM Memory CRC error, Flash chip
4 | 44 | Firmware upgrade invalid image
5 | 46 | Firmware upgrade error
6 | 53 | RTC circuit error
7 | 60 | Product was not approved
Number | Warning ID | Description
1 | 1000 | U1 missing
2 | 1001 | U2 missing (and it is not single-phase system)
3 | 1002 | U3 missing (and it is not single-phase system)
4 | 1003 | Not Locked device, not set password
5 | 1008 | Frequency out of the metering limit
6 | 1010 | Date not set
7 | 1011 | Time not set
8 | 1012 | U2 connected for single phase wires setup
9 | 1013 | U3 connected for single phase wires setup
10 | 1014 | I1 missing
11 | 1015 | I2 missing (and it is not single-phase system)
12 | 1016 | I3 missing (and it is not single-phase system)
13 | 1017 | I2 connected for single phase wires setup
14 | 1018 | I3 connected for single phase wires setup
15 | 1040 | U1, U2 and U3 are inverse in 3 phases system
16 | 1041 | I1 wrong direction
17 | 1042 | I2 wrong direction (and it is not single-phase system)
18 | 1043 | I3 wrong direction (and it is not single-phase system)
19 | 1044 | I1 and I2 are inverse (and it is not single-phase system)
20 | 1045 | I2 and I3 are inverse (and it is not single-phase system)
21 | 1046 | I3 and I1 are inverse (and it is not single-phase system)
22 | 1047 | Measurement value too big can not display on the displayer
Number | Alarm ID | Description
1 | 2013 | alarm 1
2 | 2014 | alarm 2
3 | 2015 | alarm 3
4 | 2016 | alarm 4
5 | 2017 | alarm 5
6 | 2018 | alarm 6
7 | 2019 | alarm 7
8 | 2020 | alarm 8
9 | 2021 | alarm 9
10 | 2022 | alarm 10
11 | 2023 | alarm 11
12 | 2024 | alarm 12
13 | 2025 | alarm 13
14 | 2026 | alarm 14
15 | 2027 | alarm 15

## Changes
Map version | Date | Changes
V1.0_20230404 | 04/04/2023 | First integrate version
V1.0_20230606 | 06/06/2023 | 1. Added "Digital Input 1 energy" and "Digital Input 2 energy" regs. 2.All logs added one more reg to read the Total Entry Numbers. 3."Slave ID" changed to "Linear Slave ID". 4. Removed "Product type number ID". 5. Changed to "256=DI1, 512=DI2, 32768=LED" in I/O Port Pulse configuration. 6. Added "5=import SEN total, 6=export SEN total" in I/O Port Pulse configuration. 7. “Specialday - Day ID, 1~Total number” changed to "Specialday - Entry ID, 1~Total number". 8. Removed "LED source".
V1.0 | 09/11/2023 | 1. Changed the "Threshold of Alarm" resolution from 1 to 0.001 in order to adapt power factor setting. 2. Changed the maximum value of Alarm threshold in sheet "OBIS code". 3. Reorgnize document format.
V1.1 | 2024-05-07 | 1. Changed the SlaveID of D1M20 Ethernet product to the same as D1M20 Modbus product, that is 149. 2. Changed the data format of timer up counter and timer down counter as 0.1 resolution.